## Forward_Test
ID | Exact proposal sentence (para ref) | Entity & stage | Location/system | Tender Schedule line | Source drawing/spec/addendum + rev | Quantity basis | Material/subcontract rate basis | Labour allowance | Plant & access allowance | Preliminaries treatment | Workbook sheet/row/cost code | External treatment | Confidence | VERDICT | FINDING
FT-01 | §2/Table 2/Table 3: Stage 1A $2,761,814.98 + WSUD PC $111,787.74 = $2,873,602.72; Stage 1B $113,131.26; TOTAL $2,986,733.98 ex GST | TCS – 1A & 1B | Whole package | All | N/A – tie-out | N/A | N/A | N/A | N/A | N/A | 'TCS $ Sched' D24/D31/D32/D44/D46; Sched3_Extract R8/R10/R12/R23 | Table 2 & Table 3 of submission | High | PASS | Every headline figure in the docx ties to the cached workbook value to the cent, and Sched3_Extract's helper build (R8=D24-F67; R12=F67; R23=D44) reconciles the 1A stormwater/GT split without double-counting. No figure in the submission fails to tie to the model.
FT-02 | §4 bullet 1: 'The civil stormwater network to the roads, carpark, netball courts and surrounds… pipe drainage, box culverts C01 to C10, precast pits and access chambers, road gully inlets, headwalls and rock protection, and the outlet works to the documented basin (Sch 3 item 2.5, incl item 2.3 drainage component)' | TCS – 1A | Civil stormwater network | 1A 2.3-a / 2.5 | F1300–F1305, F1310, F1320–F1325, F1350–F1363, all T1 17/06/26 | 141 structures adopted (121 F1310 + 20 C-series, incl C09A/B) per QUANTITY_RECONCILIATION TCS_Civil | Materials_Master P1-P13,F1-F8,C1-C6,H1-H11,S1-S10,R1/R3 (Humes/Reece project quotes + benchmark rows) | Stage1A_Drainage A-03–A-07,B-01–B-06,C-01–C-04 crew-days | Excavators (13-16T/8T/20-24T/3-5T), crane/franna, breaker – Stage1A_Drainage C block | 5.5% on total cost (TCS $ Sched C8) | Stage1A_Drainage rows 6-71 (materials), 77-99 (labour), 108-122 (plant); Sched3_Extract R8 = $2,204,088.48 | Table 3 row '1A-2.5 Stormwater drainage'; Noted Inclusions §8.2 | Medium | PASS | Complete material+labour+plant+prelims chain for the drainage-network claim. VOL 35 (governing civil spec) absent — compliance-basis ceiling per RUN_STATUS/Risk Register D6 (§12 rule): section confidence capped Medium regardless of drawing traceability.
FT-03 | §4 bullet 2: 'Runs GT1 to GT4 and GT7 to GT9 with their trash boxes, end caps and connection pits, including their excavation and quarry material (Sch 3 item 3.5)' | TCS – 1A | Netball court/walkway trench drains | 1A 3.5 | F1320 GT schedule T1; TENDER_PROMPT §5.3 locked reinstatement instruction ('Denis also set aside the excavation and quarry for these — reinstate that too') | 561.9 m (608.5 m GT total less 46.6 m to 1B) + 29 trash boxes (25 TB200+4 TB100) adopted | Materials_Master M48-M54 (Hauraton Recyfix, Reece quote) | Stage1A_Drainage C-06 (23cd) + C-07 (13cd) | 3-5T excavator (part of the 56 total days) + quick-cut saw (5d) | 5.5% on total cost | Stage1A_Drainage rows 54-58 (materials), 101-102 (labour); Sched3_Extract R12/R61-67 (GT helper build) | Table 3 row '1A-3.5 Grated trench drains and pits' $557,726.50; Noted Inclusions §8.3 | Medium | PARTIAL | Trash-box/channel supply and installation labour are fully priced and tie exactly. But the 'quarry material' limb of this specific claim has NO identifiable cost: Stage1A_Drainage's only bedding-stone line (Q1, formula =0.203×Σ pipe metres) explicitly sums P1,P3,P5-P9,P11-P13 — the mainline/collector/DWV rows — and does NOT include G1/G2 (the GT channel rows). No other material row represents GT trench bedding or quarry stone anywhere in Stage1A_Drainage, Stage1B_Drainage or Materials_Master. This is a direct, named locked-decision item (§5.3) that is not demonstrably costed as stated. Exposure: unquantified — no cost line exists to measure a variance against; a fresh estimate is needed, not an inference from the pipe-trench bedding rate.
FT-04 | §4 bullet 3: 'Installation of the stormwater filtration manhole and its cartridges, the cartridge and internals supply and delivery being carried separately as a prime cost sum (Sch 3 item 2.5)' | TCS – 1A | WSUD DN3300 manhole, SW corner of courts | 1A 2.5 | RPT006_B §7.4 (Addendum 8); F1324 T1 | 1 manhole, 22 cartridges (Design Report nomination) | Reece Q-459014431 (project-specific, current); freight separately identified | Stage1A_Drainage C-05 (8cd, in BASE lump sum) | 20-24T excavator (rock/WSUD share) + 50t crane share (allowance) | 5.5%/18%/18% on the BASE lump sum only – PC sum carries its own +15%, not the 41.5% chain | 'TCS $ Sched' D27-D31; Stage1A_Drainage row 100 (C-05) | Table 2/3/4; §9 Provisional Sums and Prime Cost Sums | Medium | PASS | Correctly split – the PC sum is supply+delivery ONLY and installation is named as sitting in the base lump sum (§9 second paragraph is explicit on this), which is precisely the discipline Rule 4's fixture/equipment test requires. Confidence capped Medium because the $90,064.63 Reece rate is the ONLY project-specific price and is internally flagged (Register Gap #1/Opens #10) against an Ocean-Protect-derived benchmark of ≈$77.7k pre-freight (18-cart $70,060 / 13-cart $60,460 → ≈$1,920/cartridge increment, ≈$35.5k base + 22×$1,920 ≈ $77.7k) — a ≈16% gap not yet reconciled by a direct Ocean Protect re-quote on the actual MUSIC model. See Findings #3.
FT-05 | §4 bullet 4: 'The civil stormwater within the Stage 1B extent: grated trench runs GT5 and GT6 with their trash boxes and end caps, and drainage lines 60, 61 and 83 with their connections (Sch 3 item 2.3)' | TCS – 1B | District park/PAM stormwater + multi-use court/amenities trench drains | 1B 2.3 | F1303 (1B extent), F1310/F1320 T1 | 46.6 m GT5+GT6 + 4 TB100 + 29.6 m 150 PVC (lines 60/61/83) | Materials_Master M50/M59-M60/M21 (Reece quote) | Stage1B_Drainage C-08 (3cd) + C-09 (4cd) | 3-5T excavator (7d) + tipper (1d) + water truck (1d) | 5.5% on total 1B cost | Stage1B_Drainage rows 6-13 (materials), 19-22 (labour) | Table 3 row '1B-2.3 Stormwater drainage' $113,131.26; Noted Inclusions §8.4 | Medium | PARTIAL | Same quarry-material gap as FT-03 applies to GT5/GT6 (Stage1B_Drainage G1/G2, rows 7-8) — no bedding/quarry material line exists for these rows either. Lines 60/61/83 (plain PVC DWV) are fully and correctly costed with no gap.
FT-06 | §7.2: 'Pipework is priced in the documented material mix… reinforced concrete pipe in Class 3 with Class 4 where nominated, polypropylene collectors… and PVC-U DWV where drawn. Box culverts are precast reinforced concrete units… Precast pits, chambers, gully inlets, grates, frames and covers are priced to the CMDG standard details' | TCS – 1A/1B | Materials basis | 1A 2.5 / 1B 2.3 | F13xx series T1; CMDG-D-020/030 | 714.9 m RCP (702.9 CL3+12.0 CL4), per-line PP/DWV splits per QUANTITY_RECONCILIATION | Materials_Master M01-M48 (Humes REV2 + Reece, project-specific, current to Aug-2026) | (covered under FT-02/FT-24 etc.) | (covered under FT-02) | (as above) | Materials_Master full column; Stage1A/1B_Drainage material blocks | §7.2 Civil Basis paragraph | Medium | PASS | Materials basis matches the adopted quantities and current quotes. VOL 35 (governing civil spec) absent — compliance-basis ceiling per RUN_STATUS/Risk Register D6 (§12 rule): section confidence capped Medium regardless of drawing traceability. Specifically: pipe class/wall-thickness and precast structural design conformance are only verifiable against CMDG + the drawings; if VOL 35 imposes a different material class or additional testing regime, this claim's compliance basis — not its quantity — would need revisiting.
FT-07 | §7.3: 'We have priced trench and structure backfill compacted and tested to 98% Modified maximum dry density in trafficable areas, in accordance with the specification tables… Testing and flushing… CCTV… and a pre-completion drainage clean and de-silt are included' | TCS – 1A/1B | Compaction/testing/CCTV | 1A 1.6 / 1B 1.6 | H002 note 17 (duplicate of n.16, so no drawn compaction spec); 'specification tables' unnamed | 40 tests (1A) + 4 tests (1B); CCTV qty formula-driven (1,667 m = sum of priced pipe metres) | Materials_Master H85 ($140.30/test) + H82 ($5.75/m CCTV, benchmark-derived off VOL38 §3.56 obligation) | Stage1A_Drainage A-09 (4cd) + Stage1B A-13 (2cd) | N/A | Funded partly from bottom-up Prelim_OH (CCTV/ADAC/RPEQ/clean) and partly from stage subbies (compaction) | Stage1A_Drainage row 128 (F128); Stage1B row 35 (F35); Prelim_OH rows 24/26/27 | §7.3 Civil Basis paragraph; Noted Inclusions §8.1 bullets 7–9 | Medium | PASS | Costed and formula-linked to actual priced pipe metres — a materially stronger position than the TPS package's equivalent compaction-testing item (which was NBC-only and zero on the longest-trench work area). One open item: the docx's phrase 'in accordance with the specification tables' does not name which specification. VOL 38 (hydraulic spec, present) §3.62 is the only compaction table on file; VOL 35 (the actual governing civil spec) is absent. The submission should not let a borrowed hydraulic-spec table stand in for the missing civil spec — see Finding #7.
FT-08 | §7.4: 'The units are priced as drawn, with the bedding extra-over that regime requires. Surface tie-in, load-class upgrades and any protection slab over the units are excluded' | TCS – 1A | Culverts C01-C03, C05-C08, C10 (zero/negative cover) | 1A 2.5 | F1350-F1363 long sections | 130.76 m RCBC at zero/negative cover | Materials_Master H72 (bedding stone, culvert extra-over Q2) | (within C-01/C-02/C-03 crew-days) | (within excavator days) | 5.5% on cost | Stage1A_Drainage row 63 (Q2, $3,224) | §7.4 Civil Basis; Exclusions §12.1 ('hardstands… outside the drainage structures specifically measured') | High | PASS | Exact, named, quantified extra-over bedding cost; the exclusion of surface tie-in/protection slab is stated in the same breath — a model example of Rule 4 boundary drafting (names what's excluded and why, immediately next to what is priced).
FT-09 | §7.5: 'Every structure scheduled on F1310 and every line drawn on the civil sheets — including lines 81, 83 and 87 in full — is priced in this submission, and we receive and connect the building downpipe stubs into our lines and pits at the nominated civil connection points' | TCS – 1A/1B | Building stormwater POD boundary | 1A 2.5 / 1B 2.3 | F1303 note (AS 3500.3); H-NBC-101/H-PAM-101 'CONNECT TO CIVIL' stubs | 141 structures (121 F1310 + 20 C-series) adopted, incl lines 81/83/87 | Materials_Master P11 (line 81 225 DWV 115.45m adopted, printed chainage governs, Denis's 180.93m over-measure removed) | Stage1A_Drainage A-06/C-07 etc. | (as above) | (as above) | Stage1A_Drainage row 16 (P11) | §7.5 Civil Basis; Exclusions §12.1 ('every structure and line drawn on the civil sheets from the nominated civil connection point onward, and the connection into our line or pit is ours') | Medium | PASS | This is the corrected POD boundary per SCOPE_MATRIX Appendix (i) C-1 and matches TPS's mirror-image exclusion exactly — checked against 01_SCOPE_MATRIX.md 2.5-x5/Appendix (iii) L2, no double-count and no gap found in either direction. VOL 35 (governing civil spec) absent — compliance-basis ceiling per RUN_STATUS/Risk Register D6 (§12 rule): section confidence capped Medium regardless of drawing traceability.
FT-10 | §7.6: 'The 100 mm subsoil drainage, re-nominated by the Design Report as a type 2 strip-filter system, is by others. We accept strip-filter and subsoil connections at our collector pits only… the outlet connections received at our pits are priced. The strip-filter system, its media and its collector pipework are not priced' | TCS – 1A/1B | Subsoil/strip-filter interface | 1A 2.3-x2/2.5-x3 | F1320 T1; RPT006_B §6.1 (Add 8); CMDG-D-040/041 | 283.71 m of 100 PVC outlet/DP laterals adopted (connections only, not the strip-filter system itself) | Materials_Master M12 (100 PVC DWV) | Stage1A_Drainage A-07 | N/A | N/A | Stage1A_Drainage row 18 (P13), note 'Subsoil SYSTEM excluded by others; outlets/connections at TCS pits only' | Exclusions §12.1; §7.6 Civil Basis | High | PASS | Correctly and precisely bounded: the connection is priced, the excluded system is not — mirrors Change Log D4's decision not to reinstate the old model's orphaned $10,865 subsoil-pipe formula, which is the right call since that scope is excluded, not merely uncosted.
FT-11 | §7.7: 'At the basin we stop at structural backfill of our own pipes, pits, culverts and outlet structures. The outlet box culvert, its headwalls and the rock pads… are priced. Basin bulk shaping, embankment earthworks, the concrete spillway weir… are not priced' | TCS – 1A | Detention basin interface | 1A 2.5 | F1305 T1; F1323 T1; RPT006_B | 2700x1200 outlet culvert (C6, 8 units) + BCC headwalls (H11, 2 units) + basin rock pads (R3, 236.997 m3) | Materials_Master M27/M38/H73 | Stage1A_Drainage C-01 (6cd, C10 outlet) + B-08 (part, rock pads) | 50t crane (C10 heavy-lift share) | 5.5% on cost | Stage1A_Drainage rows 32,43,61 (materials), 96 (labour); row 65 (X1, basin earthworks/spillway = $0, held on EBC E2) | §7.7 Civil Basis; Query B5 | High | PASS | Textbook Rule 5 'no silent zero' treatment: the excluded basin-shaping/spillway scope is carried at an explicit $0 flagged row in the base model (X1) AND has a fully backed add-price on the EBC sheet ($52,523.57, E2) ready for reinstatement — exactly the discipline TENDER_PROMPT §5 and §9.2 require.
FT-12 | §7.8/§8.1: 'As-constructed survey pick-up, RPEQ-certified as-constructed drawings and ADAC-compliant XML data for our own stormwater assets are included, together with CCTV of our own in-ground drainage' | TCS – 1A/1B | As-constructed deliverables | 1A/1B 1.6 | ITT §19; VOL 38 §3.56; Sch item 1.6 both stages | 1 lot ADAC + 1 lot RPEQ + CCTV per priced metres (1,667 m formula) | Materials_Master H82 (CCTV rate) | Stage1A_Drainage A-10 (3cd) | N/A | Prelim_OH rows 24-26 (CCTV $9,585.25, ADAC $4,500, RPEQ $3,500) — funded from the 5.5% pool | Prelim_OH rows 24-26; Stage1A_Drainage row 86 | §7.8; Noted Inclusions §8.1 bullets 6-7 | High | PASS | RPEQ certification specifically HAS a cost line here ($3,500 lot) — this is the exact item that FAILED on the TPS side of this same tender (TPS FT-32/RT-14, zero RPEQ cost found anywhere in that model). TCS gets this right.
FT-13 | §8.1 bullet 1: 'Establishment, maintenance and removal of TriCore Civil Services’ own site compound for the included works, including fencing, gates, signage, and the vegetation-management wash-down and rumble grid provision' | TCS – 1A | Site establishment | 1A/1B 1.1 | ITT §17.1-17.3; VFMP | 3 crew-days + 1 lot compound | Materials_Master (none direct – Prelim_OH allowance) | Stage1A_Drainage A-01 (3cd) | N/A | Prelim_OH row 8 ($4,500 lot, VFMP washdown/rumble grid/signage) | Stage1A_Drainage row 77; Prelim_OH row 8 | Noted Inclusions §8.1 bullet 1 | Medium | PASS | Funded from the 5.5% prelim pool, consistent with the non-disclosure convention for prelim build-up; bottom-up line exists and is quantified (not a bare percentage assumption).
FT-14 | §8.1 bullet 2: 'TriCore Civil Services’ own temporary site services — portable toilets and wash station, generator, temporary power boards and leads, and temporary potable water storage and cartage — on the basis that no site power or water is provided… Nothing is shared with, or recharged to, any other package' | TCS – 1A/1B | Temporary services | 1A 2.2-b / 1B 2.1-a | ITT §17.3 | 26 weeks toilets/genset/power + 1 lot water cartage | N/A (subbie/hire allowance) | (within A-01 establishment days) | N/A | Prelim_OH rows 17-20 ($3,120+$3,380+$6,000+$650=$13,150) | Prelim_OH rows 17-20 | Noted Inclusions §8.1 bullet 2 | Medium | PASS | Bottom-up itemised, matches the locked §5.1/§5.2 'nothing shared' rule — no cross-subsidy with the TPS model (verified: TPS's Prelim_OH is a wholly separate cost pool in a separate workbook).
FT-15 | §8.1 bullet 3: 'Delineation of our own work areas with bollards, pickets and barrier mesh, site management, site PPE and consumables, and general waste containment' | TCS – 1A/1B | Site management | 1A/1B 1.1 | N/A | 6 months each line | N/A | (within A-01/A-02) | N/A | Prelim_OH rows 11-13,15 ($2,400+$1,080+$2,400+$3,600=$9,480) | Prelim_OH rows 11-13,15 | Noted Inclusions §8.1 bullet 3 | Medium | PASS | Itemised bottom-up, ties cleanly.
FT-16 | §8.1 bullet 5: 'Trade set-out survey… Dial Before You Dig enquiry and service location, including a specialist locating attendance over the existing irrigated playing fields' | TCS – 1A/1B | Set-out/services location | 1A/1B 1.5 | N/A (geotech §2.0 re: live irrigation) | 3 crew-days + surveyor 5d + locator 1d | Materials_Master H83-H84 | Stage1A_Drainage A-02 (3cd) | N/A | N/A | Stage1A_Drainage row 78 (A-02); rows 126-127 (surveyor/locator) | Noted Inclusions §8.1 bullet 5 | High | PASS | Named 'specialist locating attendance over… irrigated playing fields' maps exactly to the 'Services locator (live irrigation under ex-fields, geotech S2.0)' subbie row — precise, not generic.
FT-17 | §8.1 bullet 9: 'Compaction testing to the trench and structure reinstatement of the included works' | TCS – 1A/1B | Compaction testing | 1A/1B 1.6 | VOL38 §3.62 (borrowed – see FT-07) | 40 tests (1A) + 4 tests (1B) | Materials_Master H85 | N/A (subbie) | N/A | N/A | Stage1A_Drainage row 128; Stage1B row 35 | Noted Inclusions §8.1 bullet 9 | Medium | PASS | Quantified on BOTH stage sheets — unlike the TPS package's equivalent claim (package-wide wording, NBC-only cost, zero at the two work areas with the longest trench runs), TCS's compaction-testing claim is backed everywhere it is made.
FT-18 | §8.1 bullet 10: 'Site supervision and project management of the included works' | TCS – 1A/1B | Supervision/PM | 1A/1B 1.7 | N/A | 114.1 LH-days (1A) + 5.9 LH-days (1B), pro-rata to crew-days | N/A | Stage1A_Drainage A-14 ($151,711.27); Stage1B A-14 ($7,844.84) | N/A | Direct labour (NOT a preliminary) — see TCS_CHANGE_LOG.md §9 | Stage1A_Drainage row 104; Stage1B row 24; Prelim_OH row 6 (retained at $0 for traceability) | Noted Inclusions §8.1 bullet 10 | High | PASS | Well-evidenced correction: the departure (an earlier V2 build placed LH supervision inside the 5.5% pool) was found, the primary evidence (old Civ 'SW Zone Sumry' B13) was cited, and the fix is auditable end-to-end. This is the single largest, best-documented correction in the whole model ($225,771.90 net commercial effect).
FT-19 | §8.1 bullet 11: 'One remobilisation allowance for the EDQ review gate ahead of stormwater commencement (Conditions 16 and 17)' | TCS – 1A | Programme gate | 1A 1.1 | RPT006_B §3.1, EDQ Conditions 16/17 | 4 crew-days + 2 plant-float loads | N/A | Stage1A_Drainage A-11 (4cd) | N/A | Prelim_OH row 22 ($1,600, 2 loads) | Stage1A_Drainage row 87; Prelim_OH row 22 | Noted Inclusions §8.1 bullet 11; Qualifications §12.2 | High | PASS | One remobilisation only — matches the qualification wording exactly ('One EDQ-gate remobilisation is allowed'), no over-claim.
FT-20 | §8.2 bullet 1: 'Supply and installation of the reinforced concrete pipe stormwater mainline in Class 3, with Class 4 where nominated, including the twin-barrel C09 crossing and the rubber ring joints' | TCS – 1A | RCP mainline | 1A 2.5 | F1300-F1305 layouts; F1304 (C09) | 714.9 m (702.9 CL3 + 12.0 CL4) + 293 rubber rings | Materials_Master M01/M02 (Humes REV2, project-specific, current) | Stage1A_Drainage A-03 (16cd) + A-04 (1cd) | 13-16T/20-24T excavators (part) | 5.5% on cost | Stage1A_Drainage rows 6-9 (materials), 79-80 (labour) | Noted Inclusions §8.2 bullet 1 | Medium | PASS | Full chain present. C09A/B headwalls priced as standard precast (2 units, H2, $1,177.60) is explicitly qualified as at-risk if non-standard (Query B1) — correct disclosure, not a silent assumption.
FT-21 | §8.2 bullet 2: 'Supply and installation of the polypropylene collector mains to the court bays and the tank line' | TCS – 1A | PP collectors (225/300/375/450/600) | 1A 2.5 | F1300-F1305 layouts | 58.56-210.43 m per diameter, adopted per QUANTITY_RECONCILIATION | Materials_Master M05-M09 (Reece project quote for 225/375/600; M06/M08 300mm/450mm are INTERPOLATED, not quoted) | Stage1A_Drainage A-05 (10cd) | (part of excavator days) | 5.5% on cost | Stage1A_Drainage rows 10-14 (materials), 81 (labour) | Noted Inclusions §8.2 bullet 2 | Medium | PASS | 300mm and 450mm PP rates are derived by interpolation between quoted 225/375/600 rates, not themselves quoted (Materials_Master I16/I18 note 're-quote at award'). Low materiality (≈$12.6k combined) but confidence for those two specific lines is Medium-Low, not Medium-High.
FT-22 | §8.2 bullet 3: 'Supply and installation of the PVC-U DWV building drainage collector on line 81 and the trash box laterals' | TCS – 1A | Line 81 + trash box laterals | 1A 2.5 | F1303 note; F1310 | 115.45 m (line 81, printed chainage adopted over Denis's 180.93 m) + 33.25 m laterals | Materials_Master M10/M11 (Tradelink, project-specific) | Stage1A_Drainage A-06 (2cd) + C-07 (part) | (part of excavator days) | 5.5% on cost | Stage1A_Drainage rows 16-17 (materials), 82 (labour) | Noted Inclusions §8.2 bullet 3 | High | PASS | Quantity change from Denis's 180.93 m to the adopted 115.45 m is retained and reasoned (printed design data governs) — consistent with Rule 3 (never hide a difference by overwriting a cell).
FT-23 | §8.2 bullet 4: 'Supply and installation of the 100 mm PVC-U outlet and downpipe laterals received and connected at our pits' | TCS – 1A | 100 PVC outlets/DP laterals | 1A 2.5 | F1303; F1310 | 283.71 m adopted | Materials_Master M12 (Reece project quote) | Stage1A_Drainage A-07 (4cd) | (part) | 5.5% on cost | Stage1A_Drainage row 18 (P13), row 83 (labour) | Noted Inclusions §8.2 bullet 4 | High | PASS | Correctly scoped to 'received and connected' only — does not overreach into the excluded subsoil system (cross-ref FT-10).
FT-24 | §8.2 bullet 6: 'Supply and installation of the precast reinforced concrete box culverts — 600×300, 750×300 including the WSUD high-flow bypass, 900×450, 1200×600, 1500×600 and the 2700×1200 units at the basin outlet' | TCS – 1A | Box culverts C01-C10 | 1A 2.5 | F1350-F1363 long sections | 70 crown units across 6 sizes, per adopted lengths/2.4m modules | Materials_Master M22-M27 (Humes REV2, project-specific, current) | Stage1A_Drainage C-01,C-02,C-03 (23cd) | 20-24T excavator + 50t crane/franna share (C10, C-01) | 5.5% on cost | Stage1A_Drainage rows 27-32 (materials), 96-98 (labour) | Noted Inclusions §8.2 bullet 6 | Medium | PASS | Complete chain. Confidence Medium reflecting the crane/franna allowance flag (FT-29) and the Humes-vs-Reece take-off discrepancy noted at source (RCP375 299 vs 262 lengths; our adopted 714.9 m governs, quantity risk disclosed).
FT-25 | §8.2 bullet 7: 'Supply and installation of the precast headwalls to the pipe outlets and to the box culvert end structures, including wingwalls and the beaching interface' | TCS – 1A | Headwalls H1-H11 | 1A 2.5 | F1350-F1363 | 20 headwalls (11 pipe-type H1-H5 + 9 culvert-type H6-H11, wait: actual model = 5 pipe headwall types + 6 culvert headwall types) | Materials_Master M28-M38 (Reece/Humes/Jaybro mix, project-specific) | Stage1A_Drainage B-06 (10cd) + C-04 (16cd) | (part of excavator days) | 5.5% on cost | Stage1A_Drainage rows 33-43 (materials), 93,99 (labour) | Noted Inclusions §8.2 bullet 7 | Medium | PASS | Full chain; C09A/B twin-cell headwall (H2, 2 units) carries the same standard-assumption qualification as FT-20.
FT-26 | §8.2 bullet 8: 'Supply and installation of road gully inlet units on grade and in sag to CMDG-D-020' | TCS – 1A | RGU inlets | 1A 2.5 | CMDG-D-020 | 33 units (28 on-grade + 5 sag) | Materials_Master M39 — 'Old Civ workbook allowance (benchmark — NO current RGU quote: sourcing gap)' | Stage1A_Drainage B-01 (22cd) | (part of excavator days) | 5.5% on cost | Stage1A_Drainage rows 44-45 (materials, $44,550 combined), 88 (labour) | Noted Inclusions §8.2 bullet 8 | Low | PASS (rate flag) | Installation is fully priced and correctly claimed. But the $1,350/ea supply rate for the single largest precast-pit material line ($44,550 across 33 units) is explicitly self-flagged in Materials_Master as a 'sourcing gap' with no current quote — it is a benchmark carried from the old Civ workbook. See Finding #4.
FT-27 | §8.2 bullet 9: 'Supply and installation of 1050 dia access chambers to CMDG-D-030 with cover slabs, the 1200 chambers including the internal upstand at chamber 26-02, the 600 × 600 field inlet pits, and the grates, frames and covers to the included structures' | TCS – 1A | Access chambers/field inlets | 1A 2.5 | CMDG-D-030; F1310 (26-02 upstand) | 13×1050 chambers + 4×1200 chambers + 3×600 field inlets + grates/frames/covers | Materials_Master M40-M47 (mix of Tradelink and benchmark rows) | Stage1A_Drainage B-02 (13cd) + B-03 (6cd) + B-04 (2cd) | (part) | 5.5% on cost | Stage1A_Drainage rows 46-53 (materials), 89-91 (labour) | Noted Inclusions §8.2 bullet 9 | Medium | PASS | 26-02 internal upstand (0.467 m) is specifically called out in both the material row (S6) and the labour note ('upstand formwork in labour B-03') — traced end to end.
FT-28 | §8.2 bullet 10: 'Rock protection to our own structures — beaching to the culvert headwalls and the rock pads at the basin inlet and outlet' | TCS – 1A | Rock beaching/pads | 1A 2.5 | F1350-F1363; F1305 | 25.34 m3 (headwall beaching) + 32.32 m3 (general) + 236.997 m3 (basin pads) | Materials_Master H73-H74 (benchmark rates, old Civ workbook) | Stage1A_Drainage B-08 (9cd) | (part of excavator days) | 5.5% on cost | Stage1A_Drainage rows 59-61 (materials), 95 (labour) | Noted Inclusions §8.2 bullet 10 | Medium | PASS | Priced and installed; rate basis is a benchmark carry-forward (no live quote for rock beaching specifically), lower materiality than the RGU gap (≈$32.7k combined).
FT-29 | §8.2 bullet 13: 'Cranage and lifting for the heavy precast elements — the basin outlet box culvert units, the filtration manhole and the large headwalls — by mobile crane and pick-and-carry' | TCS – 1A | Heavy-lift cranage | 1A 2.5 | N/A (construction methodology) | 8 crane-days + 17 franna-days | N/A | (covered elsewhere) | Equip_Master D16/D17 — flagged 'ALLOWANCE — not in hire registers, quote at award' (both lines) | 5.5%/18%/18% on cost | Stage1A_Drainage rows 116-117 ($30,400 + $37,400 = $67,800 pre-markup) | Noted Inclusions §8.2 bullet 13 | Low | PASS (rate flag) | The activity IS priced and the claim is true in direction, but the $67,800 combined crane/franna cost rests on an internal day-rate allowance with no confirmed hire-house quote anywhere in the register — explicitly self-flagged on Equip_Master. See Finding #6.
FT-30 | §8.2 bullet 14: 'Trench shielding for the runs and structures requiring personnel entry, and geotechnical inspection attendance at the deep excavations' | TCS – 1A | Trench support/geotech inspection | 1A 2.5 | NQL2024-0320 §5.3.3 | 14 shield-days + 4 geotech visits | N/A | (covered elsewhere) | Equip_Master D18 — flagged 'ALLOWANCE — not in hire registers' | 5.5%/18%/18% on cost | Stage1A_Drainage row 118 ($1,680); Materials_Master H86/row 129 ($3,910, geotech inspections) | Noted Inclusions §8.2 bullet 14; Query A3 | Low | PASS (rate flag) | Geotech inspection subbie rate is a named estimator benchmark (defensible, low value). Trench shield day-rate ($120/day) is unconfirmed against any hire register — same class of gap as FT-29 but lower dollar value.
FT-31 | §8.2 bullet 15: 'Non-destructive (vacuum) excavation where our trenches enter tree protection zones' | TCS – 1A | TPZ vacuum excavation | 1A 2.5 | VFMP (CONFLICT_LOG G) | 6 days | N/A | N/A | Equip_Master D13 (hire-register rate, Y) | 5.5% on cost | Stage1A_Drainage row 119 | Noted Inclusions §8.2 bullet 15 | High | PASS | Confirmed hire-register rate, correctly and narrowly scoped to TPZ entry only.
FT-32 | §8.2 bullet 16: 'Dewatering of our own excavations by the site sump-pump set' | TCS – 1A | Dewatering | 1A 2.5 | NQL2024-0320 §5.4.2 (groundwater/seepage) | 10 days | N/A | N/A | Equip_Master D14 (hire-register rate, Y) | 5.5% on cost | Stage1A_Drainage row 121 | Noted Inclusions §8.2 bullet 16; Exclusions §12.1 ('dewatering beyond that manageable by the site sump-pump set… excluded') | High | PASS | Confirmed hire-register rate; the exclusion is correctly paired in the same section to bound the claim (wellpointing/sustained control excluded).
FT-33 | §8.2 bullet 17: 'An allowance for excavation within the rock band described at Section 3.4, including hydraulic breaker attendance' | TCS – 1A | Rock excavation allowance | 1A 2.5 / 1A 7.0 | NQL2024-0320 (refusal 25/36 locations, shallowest 0.70 m) | 10 crew-days (≈15% of trench metres at reduced production) | N/A | Stage1A_Drainage A-08 (10cd) | Hydraulic breaker (10d) + 20-24T excavator share | 5.5% on cost | Stage1A_Drainage row 84 (labour); row 112 (breaker plant) | Noted Inclusions §8.2 bullet 17; §3.4 Basis of this Tender | High | PASS | Directly sourced from the geotech report (not VOL 35) — not subject to the civil-spec confidence ceiling. Extra-over rate schedule (Section 10) correctly kept separate for rock beyond this band.
FT-34 | §8.2 bullet 18: 'Installation of the WSUD filtration manhole and the 22 filtration cartridges — excavation, bedding, cranage, placement, connection of the inlet, outlet and high-flow bypass, and backfill. Cartridge supply and delivery is the prime cost sum at Section 9' | TCS – 1A | WSUD manhole install | 1A 2.5 | RPT006_B §7.4 | 1 manhole install activity | N/A (install only – supply is the PC sum, see FT-04) | Stage1A_Drainage C-05 (8cd) | 20-24T excavator + 50t crane share | 5.5%/18%/18% on the BASE cost only | Stage1A_Drainage row 100 | Noted Inclusions §8.2 bullet 18; §9 PC Sum section | High | PASS | This is the cleanest example in the whole submission of the Rule 4 fixture/equipment test being satisfied: supply/delivery (PC Sum, +15%, separately identified) is explicitly and correctly NOT the same money as installation (base lump sum, 41.5% chain) — the two are never conflated in either the model or the wording.
FT-35 | §8.3 bullet 1: 'Supply and installation of the grated trench drainage to runs GT1 to GT4… and GT7 to GT9… including end caps' | TCS – 1A | GT channels | 1A 3.5 | F1320 GT schedule | 548.8 m (GT1-4) + 13.1 m (GT7-9) = 561.9 m | Materials_Master M48/M49/M53/M54 (Reece) | Stage1A_Drainage C-06 (23cd) | 3-5T excavator share + quick-cut saw | 5.5% on cost | Stage1A_Drainage rows 54-55,57-58 (materials), 101 (labour) | Noted Inclusions §8.3 bullet 1 | Medium | PASS | GT6 grate substitution question (PRO100 D400 code 47245 scheduled vs PRO200 G-tec offered by Reece) is a Stage 1B item (FT-38), not this row; this GT1-4/7-9 material selection matches the schedule (Fibretec B125 / SS heelguard) with no substitution question.
FT-36 | §8.3 bullet 2: 'Supply and installation of the trash boxes and connection pits to those runs, and the DWV laterals from them' | TCS – 1A | Trash boxes/laterals | 1A 3.5 | F1320 GT schedule | 25 TB200 + 8 end caps PRO200 + 10 end caps PRO100 + 150 DWV laterals | Materials_Master M51/M53/M54/M11 | Stage1A_Drainage C-07 (13cd) | (part) | 5.5% on cost | Stage1A_Drainage rows 56-58 (materials), 102 (labour) | Noted Inclusions §8.3 bullet 2 | Medium | PASS | GT2 '4 pits' vs the 5 trash boxes + 7 connection pits shown on the layouts is an open RFI (Query B3) — disclosed, not silently resolved either way, and correctly kept out of the priced quantity.
FT-37 | §8.3 bullet 3: 'Excavation, bedding, quarry material, backfill and compaction for the grated trench runs and their pits' | TCS – 1A | GT trench earthworks | 1A 3.5 | N/A | 561.9 m | NO IDENTIFIABLE MATERIAL LINE for GT bedding/quarry (see FT-03) | Stage1A_Drainage C-06/C-07 (labour only) | 3-5T excavator (labour-linked days only) | 5.5% on cost | N/A — no quarry/bedding material row exists for G1/G2 | Noted Inclusions §8.3 bullet 3 | Low | FAIL | Duplicate confirmation of FT-03: this sentence explicitly claims 'quarry material' as part of the GT package (echoing the locked §5.3 instruction to reinstate GT excavation AND quarry), but excavation labour and plant are the only cost components actually present — there is no bedding-stone or quarry-material cost anywhere in the model attributable to the 561.9 m of GT trench. Exposure: unquantified; a genuine gap, not an inference.
FT-38 | §8.4 bullet 1: 'Supply and installation of grated trench run GT5 at the multi-use court and GT6 at the amenities building, with their trash boxes and end caps, including excavation, bedding, quarry material and backfill' | TCS – 1B | GT5/GT6 | 1B 2.3 | F1320 GT schedule (1B extent) | 15.2 m (GT5) + 31.4 m (GT6) + 4 TB100 | Materials_Master M50 (GT6 — 'GT6 spec is PRO100 D400 code 47245; Reece offered PRO200 G-tec — substitution verify, Register Gap #7') / M49/M62/M64 | Stage1B_Drainage C-08 (3cd) | 3-5T excavator (part of 7d total) | 5.5% on cost | Stage1B_Drainage rows 7-10 (materials), 21 (labour) | Noted Inclusions §8.4 bullet 1 | Low | PARTIAL | Two issues in one bullet: (i) same quarry-material gap as FT-03/FT-37 applies here too; (ii) GT6's priced product (Reece PRO200 G-tec) is a self-flagged, unconfirmed substitution against the F1320-scheduled PRO100 D400 code 47245 — a $12,171.53 line at risk of a spec mismatch if the substitution is not accepted.
FT-39 | §8.4 bullet 2: 'Supply and installation of the PVC-U DWV drainage to lines 60, 61 and 83 with their trash boxes and connections' | TCS – 1B | Lines 60/61/83 | 1B 2.3 | F1303 (1B extent) | 29.6 m + 4 TB100 | Materials_Master M11/M62/M64 (Reece) | Stage1B_Drainage C-09 (4cd) | (part) | 5.5% on cost | Stage1B_Drainage row 6 (P1), 9-10 (G3/G4), 22 (labour) | Noted Inclusions §8.4 bullet 2 | High | PASS | Clean, complete chain, no gaps identified.
FT-40 | §8.4 bullet 3: 'Stage 1B establishment and remobilisation as a standalone award, set-out, testing, CCTV and as-constructed attendance, compaction testing and spoil handling for the Stage 1B works' | TCS – 1B | Standalone establishment | 1B 1.1-1.7 | TENDER_PROMPT §5.2 (standalone viability, locked) | 2 crew-days (A-12) + 2 crew-days (A-13) | N/A | Stage1B_Drainage A-12 (2cd) + A-13 (2cd) | N/A | Surveyor (1d) + compaction testing (4 tests) + spoil haulage — Stage1B subbies rows 34-36 | Stage1B_Drainage rows 19-20 (labour); 34-36 (subbies) | Noted Inclusions §8.4 bullet 3; Table 2 note ('viable if awarded alone') | Medium | PARTIAL | The establishment/testing/CCTV activities ARE dedicated, separately-quantified 1B line items (not a bare percentage split) — stronger than a purely proportional allocation. However, the LH supervision (Stage1B_Drainage A-14, 5.9 days) AND the accommodation/FIFO travel share (Stage1B_Drainage row 40, $5,493.38) are both derived by a pro-rata crew-day ratio against the COMBINED 1A+1B base (Stage1A_Drainage!C103 + Stage1B_Drainage!C23), not independently sized for a stand-alone 1B mobilisation. A genuinely stand-alone 1B award would very plausibly need its own full FIFO/accommodation cycle rather than a fractional share of a combined roster — the same structural risk independently identified in the TPS package's FT-01 finding. No dollar figure is assigned because no independent stand-alone-1B cost scenario exists in the model to compare against.
FT-41 | §9 (PC Sum): 'The prime cost sum covers supply and delivery of the cartridges and internals only… Installation… is included in the Stage 1A stormwater drainage lump sum and is not exposed separately… Cleaning, cartridge replacement, media renewal and any WSUD maintenance beyond the defects liability period are excluded' | TCS – 1A | WSUD PC sum boundary | 1A 2.5 | RPT006_B §7.4 | 1 lot | Reece Q-459014431 ($90,064.63 + $7,142.10 freight) | N/A (PC sum — no labour in this line) | N/A (PC sum — no plant in this line) | +15% PC markup only, no 5.5%/18%/18% chain | 'TCS $ Sched' D27-D31 | §9 second/third paragraphs | Medium | PASS | Correct and complete boundary statement — exactly what Rule 4's fixture/equipment test demands (supply vs install vs maintenance all separately and correctly bounded). Confidence Medium for the same base-rate-verification reason as FT-04 (Finding #3).
FT-42 | §10: 'Drawing H002 note 24 requires extra-over rates for soft rock and hard rock separately, for trenches and for pits. All four are tendered below, together with the unsuitable-ground rate… These rate lines carry a rate but no quantity, and therefore contribute nothing to the tendered sum' | TCS – 1A/1B | Rate schedule | 1A 7.0 / 1B 5.0 | H002 note 24; ITT §18 | 4 rock rates + 1 unsuitable-ground rate, qty = 0 by design | Build-up formula: (crew day + excavator + breaker)/production | LabourRates_Master G15 (crew-day rate) | Equip_Master D7/D9 (excavator/breaker) | 5.5%/18%/18% on the build-up cost, per rate | 'TCS $ Sched' rows 51-56 | §10 Schedule of Rates; Table 5 | High | PASS | Rates are transparently built from the same crew/plant rate library as the base lump sums (no separate, unverifiable rate source) and the 'carries no quantity' statement is literally true — F51:F55 are excluded from every SUM feeding the tendered lump sums.
FT-43 | §11 (Access and Attendance Basis) Included bullets: site access; excavation/trenching/bedding/backfill/compaction/make-safe; service location/protection/vacuum excavation; coordination and attendance on inspections/meetings/permits; one EDQ remobilisation | TCS – 1A/1B | Access basis | 1A/1B, general | ITT §17 | N/A (basis statements) | (cross-refers to FT-02/FT-31/FT-32/FT-19) | (as above) | (as above) | (as above) | (as above) | §11 Access and Attendance Basis | Medium | PASS | Four of five bullets duplicate items already tested above (PASS). The fifth — 'coordination with and attendance on Superintendent, Principal Contractor and consultant inspections, site meetings and operational permits' — has no line item of its own; it is reasonably covered by the generic 'Site admin, stationery' Prelim_OH allowance ($9,600/6 months) but is not separately named there. Low materiality soft-cost item, not elevated to a Finding.
FT-44 | §12.3 Departure 1: 'Shop drawings. Drawing H002 note 2 requires shop drawings. Shop drawings are excluded from this submission… an add-price is held and can be provided on request' | TCS – 1A/1B | Shop drawings departure | N/A (cross-cutting, matrix X1) | H002 note 2 | N/A | NO COST LINE ANYWHERE | N/A | N/A | N/A | Searched all 11 sheets and the EBC sheet in full — no 'shop drawing' cost line exists anywhere in ROK_TCS_CostModel_V2.xlsx | §12.3 Departures from the tender documents | Low | FAIL | The words 'an add-price is held' are not true of this model: EBC contains exactly three items (E1 kerb chutes, E2 basin/spillway, E3 records) and none is a shop-drawing line. This is the single clearest Rule 4/Rule 5 defect in the TCS submission, and it is the exact same failure mode independently found on the TPS side of this tender (TPS FT-39) — confirming this is a systemic drafting habit across both submissions, not a one-off. Exposure: unquantified — no cost exists to measure against; Director must build a real estimate or remove the 'add-price held' wording.
FT-45 | §12.3 Departure 2: 'Kerb chute construction… Kerb chute construction is excluded from our base price; an add-price is held and can be provided on request' | TCS – 1A | Kerb chute departure | 1A 2.3-x1 (matrix, Director decision D6-F1) | F1310; RPT006_B §6.1 | 9 chutes (03-02,03-03,04-02,13-02–18-02) | Materials_Master M69/M70/M71 | EBC row 12 (9cd) | EBC row 13 (3-5T excavator, 9d) | 5.5%/18%/18% on the EBC build-up | EBC sheet rows 5-14 ($55,429.90 total add-price) | §12.3 Departure 2; Query B8 | High | PASS | This is a genuinely backed add-price — full material/labour/plant build-up exists and is marked 'Director decision D6-F1' pending. Direct, favourable contrast with FT-44: proves the discipline CAN be done correctly in this model, which sharpens rather than excuses the shop-drawings gap.
FT-46 | §12.2 Qualification: 'Stage 1B basin. No separate Stage 1B basin is documented… The single documented basin sits within the Stage 1A hatch and its outlet works are priced once, in Stage 1A. Confirmation is requested' + §12.1 'Basin bulk shaping, embankment earthworks and the 50 m concrete spillway weir — Query B5 refers' | TCS – 1A/1B | Basin/spillway allocation | 1A 2.5 / 1B 2.3-b | F1305; VOL 20 Rev B | 1 basin, 50m spillway (unpriced) | Materials_Master H75-H77 (spillway concrete/mesh/sub-base, EBC only) | EBC row 22 (10cd, EBC only) | EBC row 23 (5d 3-5T excavator + concrete gear, EBC only) | 5.5%/18%/18% on the EBC build-up | EBC sheet rows 16-24 ($52,523.57 add-price); Stage1A_Drainage row 65 (X1, base = $0) | §12.1/§12.2; Query B5 | High | PASS | Same correct treatment as FT-45 — the excluded item is carried at an explicit $0 in the base AND has a real, quantified add-price on EBC. No silent zero.

## Reverse_Test
ID | Workbook sheet & row/cost code | Cost description | Cost (pre-markup, ex GST) | Entity & stage | External home (proposal sentence / schedule line / PC Sum / EBC / internal-only) | Internal-only? (Y/N + reason) | VERDICT | FINDING
RT-01 | Stage1A_Drainage F72 / Stage1B_Drainage F14 | Materials subtotal at escalated rates (pre-contingency) | $745,994.02 (1A) + $24,733.21 (1B) | TCS – 1A/1B | Noted Inclusions §8.2/§8.3/§8.4 supply-and-install bullets (RCP, PP, DWV, culverts, headwalls, pits, GT channels, rock) | N – externally represented by the 'supply and installation of…' bullets, not itemised by $ | PASS | Every material row traces to a named Noted-Inclusion bullet (see Forward Test FT-20–FT-39). No orphaned material line found anywhere in either stage sheet.
RT-02 | Stage1A_Drainage F73 / Stage1B_Drainage F15 | x1.18 material contingency (Directive §5.4) | $134,278.92 (1A) + $4,451.98 (1B) | TCS – 1A/1B | N/A – internal risk allowance | Y – TENDER_PROMPT §8 bars external disclosure of internal contingency | PASS | Correctly internal-only; no external sentence claims a contingency figure, consistent with the 'never externally disclose… internal contingency' rule.
RT-03 | Stage1A_Drainage F103/F105 / Stage1B_Drainage F23/F25 | Crew labour ($606,834.33 + $31,486.69) and LH supervision direct labour ($151,711.27 + $7,844.84) | $606,834.33 + $151,711.27 (1A); $31,486.69 + $7,844.84 (1B) | TCS – 1A/1B | Noted Inclusions §8.1 bullet 10 (supervision) and every 'supply and installation of…' bullet (crew labour, work described not priced) | Y for the $ figure (labour rates never externally disclosed); N for the work description (fully described) | PASS | Correctly non-disclosed by amount, fully described by activity — matches the non-disclosure rule while still giving Rule 4 traceability internally.
RT-04 | Stage1A_Drainage F123 / Stage1B_Drainage F31 | Plant (excavators, breaker, roller, tipper, crane, franna, shields, vacuum ex, sump pumps, water truck, saw) | $165,146.73 (1A) + $2,942.12 (1B) | TCS – 1A/1B | Noted Inclusions §8.2 bullets 13–17 (cranage, shielding, vacuum excavation, dewatering, rock breaker) | N – activity described (not priced) in the proposal | PASS (with caveat) | Fully homed, but $67,800 pre-markup of this total (50t crane + franna + trench shields, cross-ref FT-29/FT-30) rests on allowances explicitly flagged 'not in hire registers' — a rate-verification risk, not a homing gap.
RT-05 | Stage1A_Drainage F131 / Stage1B_Drainage F37 | Subbies & services (surveyor, services locator, compaction testing, geotech inspections, spoil haulage) | $41,975.00 (1A) + $2,999.20 (1B) | TCS – 1A/1B | Noted Inclusions §8.1 bullets 5,7,9 and §8.2 bullet 12 (spoil handling) | N | PASS | Every subbie line traces to a named bullet; spoil-haulage quantity is formula-driven off actual priced trench metres, a strong traceability example.
RT-06 | Stage1A_Drainage F134 / Stage1B_Drainage F40 | Accommodation & FIFO travel share (Option A adopted) | $105,872.42 (1A) + $5,493.38 (1B) | TCS – 1A/1B | N/A – internal cost, correctly not disclosed externally | Y – TENDER_PROMPT §8 bars external disclosure of accommodation/FIFO costs | PASS | Correctly internal-only. Allocation method (pro-rata by crew-days across a combined 1A+1B roster) is the mechanism behind the Stage-1B standalone-viability concern raised at FT-40 — noted there, not double-counted here.
RT-07 | Prelim_OH F29 vs F31 | Bottom-up TRUE preliminaries ($62,561.25) vs the 5.5% allowance actually carried in the sell ($111,747.03) | $62,561.25 bottom-up vs $111,747.03 allowance — SURPLUS $49,185.78 (bottom-up sits 44.0% BELOW the allowance) | TCS – 1A/1B | Every bottom-up line traces individually to a Noted-Inclusions §8.1 bullet (compound, temp services, admin/PPE/consumables/mgmt, EDQ remob, CCTV, ADAC, RPEQ, drainage clean) — checked line-by-line, see FT-13–FT-19/FT-12 | N/A – the allowance itself is a top-down commercial percentage, correctly non-disclosed by amount | PASS | Specifically tested per instruction: is the $49,186 surplus evidence of a cost with no external home? No — every dollar of the $62,561.25 bottom-up cost that IS incurred has a matching Noted-Inclusions sentence; there is no 'orphaned' cost sitting inside the surplus. The surplus is unconsumed headroom inside the 5.5% pool, i.e. it behaves as additional undisclosed margin rather than a masked cost. This is the OPPOSITE finding to the TPS package (which ran a $19,628 bottom-up SHORTFALL against its own allowance — a real under-funding risk). Not a Rule 4 defect on its own, but flagged as a governance/labelling item for the Director — see Finding #8.
RT-08 | Stage1A_Drainage F136 x 0.18 / Stage1B_Drainage F42 x 0.18 | Overheads (18% on total cost) | $351,326.29 (1A) + $14,391.26 (1B) | TCS – 1A/1B | N/A – corporate overhead structure | Y – margin structure never externally disclosed (TENDER_PROMPT §8) | PASS | Correctly internal-only; no external sentence describes an overhead percentage or amount.
RT-09 | Stage1A_Drainage F136 x 0.18 / Stage1B_Drainage F42 x 0.18 | Profit (18% on total cost) | $351,326.29 (1A) + $14,391.26 (1B) | TCS – 1A/1B | N/A – margin structure | Y | PASS | As RT-08. Markup sequence verified as 5.5%+18%+18% each-on-cost, no compounding — matches the directed 41.5% exactly (TCS $ Sched C11 = 0.415).
RT-10 | EBC rows 5-14 | Kerb chute add-price (materials + 9cd labour + 9d plant, x1.415) | $55,429.90 | TCS – 1A | §12.3 Departure 2 ('an add-price is held and can be provided on request') | N – explicitly and correctly disclosed as an available add-price | PASS | Genuinely backed — see FT-45.
RT-11 | EBC rows 16-24 | Detention basin earthworks + spillway add-price | $52,523.57 | TCS – 1A | §12.1/§12.2 (excluded, 'confirmation requested') | N | PASS | Genuinely backed — see FT-46.
RT-12 | EBC rows 26-32 (E3 Records) | Records of superseded/excluded items: GT drains (was $164,860.30 orphan, now reinstated in base), subsoil pipe ($10,865 orphan, correctly still excluded), rising main/pump station/$20k fees (correctly 'NOT TCS') | N/A – record-keeping rows, not additional cost | TCS – 1A/1B | §12.1 Exclusions (subsoil, roofing/DP); cross-refers to the separate TPS submission for mains/pump/fees | N/A | PASS | Strong positive finding: unlike the old V1 model, which had TWO orphaned formula blocks feeding no roll-up (Change Log D3/D4), the rebuilt V2 model was checked in full and NO orphaned or unhomed cost was found anywhere — every cost row traces either into a stage total or onto the EBC register with a stated reason. This is the reverse-test question the task specifically asks to test, and the answer for TCS is clean.
RT-13 | 'TCS $ Sched' rows 51-55 | Rock/unsuitable-ground rate build-ups (cost column E) | $168.99–$422.46/m3 (cost, pre-markup) | TCS – 1A/1B | §10 Schedule of Rates table; Table 5 of submission | N | PASS | Rate build-up formulas reference LabourRates_Master and Equip_Master directly — no free-standing, unverifiable rate.
RT-14 | Sched3_Extract rows 61-67 (GT helper build) | GT component cost/sell reconciliation (materials + labour + plant + accommodation + LH share) | $394,153.00 cost → $557,726.50 sell | TCS – 1A | Table 3 row '1A-3.5 Grated trench drains and pits' | N | PASS | Formula-audited: reconciles exactly to the Sched3_Extract R12 and Table 3 figure; no double-count against the main Stage1A_Drainage stormwater line (R8 = D24 − F67, i.e. the GT component is subtracted out of the general drainage line before being re-added at 3.5).
RT-15 | Materials_Master M39 (RGU inlet rate) | 33 RGU inlet units at a benchmark (no live quote) rate | $44,550.00 (materials only, pre-contingency) | TCS – 1A | Noted Inclusions §8.2 bullet 8 ('road gully inlet units… to CMDG-D-020') | N – activity described, not the rate itself | PASS (rate flag) | Cost has a home (the bullet describes the work), but the rate underpinning $44,550 of materials value is a carried-forward benchmark with an explicit internal note 'sourcing gap' — see Finding #4.

## Equipment_Test
Item | Supply | Delivery | Storage | Installation | Fixings/Accessories | Connection | Testing/Commissioning | Controls | Builder- or Principal-supplied | Submission wording (verbatim/paraphrase, §ref) | VERDICT | Confidence | FINDING
WSUD StormFilter 22-cartridge DN3300 precast manhole (Ocean Protect Tall (690) PSorb, RPT006_B §7.4) | PC SUM, +15% — Reece Q-459014431 $90,064.63 (cartridges + internals). Project-specific but unverified vs OP-derived benchmark ≈$77.7k pre-freight. | PC SUM, +15% — $7,142.10 freight, separately identified within the PC base ($97,206.73 total before markup). | NOT SEPARATELY PRICED — no distinct storage/handling allowance found; reasonable for direct-to-install delivery, not flagged as a defect. | BASE LUMP SUM (Stage1A_Drainage C-05, 8 crew-days) — excavation, bedding, cranage, placement, backfill. Correctly kept OUT of the PC sum. | Bundled in PC sum 'internals' description — not separately itemised, reasonable. | BASE LUMP SUM — inlet, outlet and high-flow bypass connection named explicitly in C-05 and §8.2 bullet 18. | NOT NAMED SPECIFICALLY — covered only by the generic '§7.3 testing and flushing of the included drainage' bullet; no filtration-unit-specific commissioning line. | N/A — passive gravity cartridge system, no electrical controls; correctly excluded under §12.1 ('electrical components… to any proprietary device'). | TCS (contractor)-supplied via PC Sum, not Principal-supplied — correct per RPT006_B nomination. | §9: 'The prime cost sum covers supply and delivery of the cartridges and internals only… Installation… is included in the… lump sum and is not exposed separately' | PASS | Medium | Best-practice example of the exact discipline Rule 4 requires (never say 'supplied and installed' where only one half is costed) — but PC-sum base-rate confidence is capped Medium pending a direct Ocean Protect re-quote on the actual MUSIC model (Gap #1/Opens #10), and unit-specific testing/commissioning is not named.
Precast RCP/RCBC pipes, box culverts C01-C10 and headwalls (Humes REV2 + Reece + Jaybro) | LUMP SUM — Humes Q21642316 REV2 (project-specific, current to 16/08/26) for RCP/RCBC/BCC headwalls; Reece for winged 375 headwall; Jaybro for 150/225/300 headwalls (freight adder required, separately carried). | LUMP SUM — Humes freight 35 loads @ $852 (escalated), Reece freight 11 loads @ $1,133.16, Jaybro freight lot $1,500 — all separately identified, no double-count (crane/unload excluded from freight per supplier T&Cs, carried in plant instead). | NOT SEPARATELY PRICED. | LUMP SUM (Stage1A_Drainage A-03/A-04, B-06, C-01–C-04) — named crew-day activities per culvert size/headwall type. | Rubber ring joints (P2/P4) and pipe-to-culvert connection materials (F8) separately priced. | LUMP SUM — 20 pipe-to-pipe/pipe-to-culvert connections (F8) priced explicitly. | Covered by the general §7.3 testing/CCTV/flushing bullet; culvert-specific surface tie-in/load-class upgrades explicitly EXCLUDED (§7.4) — correctly and narrowly qualified, not silently included. | N/A. | TCS (contractor)-supplied and installed — correctly worded throughout. | §8.2 bullets 1,6,7: 'Supply and installation of the reinforced concrete pipe… the precast reinforced concrete box culverts… the precast headwalls' | PASS | Medium | Complete chain with two disclosed, low-to-medium materiality risks: C09A/B twin-culvert headwalls priced as 'standard' with details 'nowhere in the issued set' (explicitly qualified, Query B1); heavy-lift cranage (50t crane/franna) is an unconfirmed hire-register allowance (≈69% of the plant total for this equipment group), not a supplier quote.
Precast stormwater pits, chambers and road gully inlets (CMDG-D-020/D-030; F1310 schedule) | LUMP SUM — mix of Tradelink (600x600 pits/grates) and old-Civ-workbook benchmark rates (1050/1200 chambers, cover slabs, RGU inlet units — explicitly flagged 'sourcing gap' for RGU, no current quote). | LUMP SUM — Tradelink freight lot $4,500; Humes/Reece freight shares cover the balance of concrete elements. Adequate. | NOT SEPARATELY PRICED. | LUMP SUM (Stage1A_Drainage B-01–B-04) — RGU (22cd), 1050 chambers (13cd), 1200 chambers incl 26-02 upstand (6cd), field inlets (2cd). | Cover slabs (S4/S7) and grates/frames/covers (S8/S10) separately priced and matched to structure type. | Bundled within the general pit-to-pipe connection allowance (F8) and the 20-24T/8T excavator trenching activity. | Covered by the general §7.3 testing/CCTV bullet. | N/A. | TCS-supplied and installed — correctly worded. | §8.2 bullets 8,9: 'Supply and installation of road gully inlet units… 1050 dia access chambers… 600×600 field inlet pits' | PASS | Low-Medium | Installation is solid, but the RGU inlet supply rate ($1,350/ea × 33 = $44,550, the single largest precast-pit material line) is a benchmark carried from the old Civ workbook with an explicit internal note that no current RGU quote exists — the weakest rate-sourcing point in the precast-pit group, see Finding #4.
Hauraton Recyfix grated trench drain system GT1-GT9 + trash boxes/end caps (Reece Q-459014445) | LUMP SUM — Reece project-specific quote, current to 16/08/26. GT6 (Stage 1B) substitution unconfirmed: F1320 schedules PRO100 D400 code 47245, Reece offered PRO200 G-tec (Gap #7, $12,171.53 at risk). | LUMP SUM — Reece freight (11 loads $12,464.76 for 1A, 1 load $1,133.16 for 1B) separately identified. | NOT SEPARATELY PRICED. | LUMP SUM (Stage1A_Drainage C-06/C-07, Stage1B_Drainage C-08/C-09) — named crew-day activities for channel install and trash-box/lateral install. | End caps (G4/G5) priced distinctly by size/type. | 150 PVC DWV laterals from trash boxes priced (C-07/C-09). | Covered by the general §7.3 testing bullet only — no GT-specific test line. | N/A. | TCS-supplied and installed — REINSTATED per TENDER_PROMPT §5.3 after Denis's original exclusion (correctly cross-referenced against the TPS submission's mirror-image exclusion of this same line, per SCOPE_MATRIX L1). | §8.3/§8.4: 'Supply and installation of the grated trench drainage… including their excavation and quarry material' | FAIL (quarry material) | Medium | The one genuine forward-test gap in the whole submission with a direct, named locked-decision provenance (§5.3: 'reinstate that too' re: excavation and quarry): channel supply, installation labour, plant and trash-box/end-cap materials are all fully priced and correctly reinstated, but NO bedding/quarry-material cost exists anywhere in the model for the 608.5 m of GT trench (Stage1A_Drainage Q1's formula explicitly excludes the G1/G2 rows) — see FT-03/FT-37/FT-38 and Finding #2. Additionally the GT6 product substitution (Gap #7) and the $198/m vs $232.94/m Fibretec rate anomaly on the 550 m Reece line (Gap noted, $19,217 — the model conservatively adopted the HIGHER rate, so this is a possible upside/negotiation point, not a pricing risk) are both disclosed internally but not mentioned in the external submission text.

## Findings_Summary
Rank | Severity | Ref(s) | Area | Finding | Dollar exposure (if quantifiable) | Recommendation before red-team
1 | CRITICAL | FT-44 | Departures (§12.3) | Shop drawings 'add-price held' claim is unbacked — no cost line exists anywhere in the EBC sheet or any other sheet in ROK_TCS_CostModel_V2.xlsx for shop drawing production, despite the submission stating one is held and available on request. Identical failure mode independently found on the TPS side of this same tender (TPS FT-39), confirming a systemic drafting habit rather than a one-off. | Unquantified — no cost exists to measure a variance against (Rule 2: flagged, not invented). | Build a genuine EBC line for shop-drawing production with a real cost build-up, or remove the 'add-price held / available on request' wording from §12.3 until one exists.
2 | CRITICAL | FT-03, FT-05, FT-37, FT-38, Equipment_Test row 4 | GT trench drains (§8.3/§8.4) | 'Excavation and quarry material' for the grated trench drains is claimed as included — and is a direct, named TENDER_PROMPT §5.3 locked-decision reinstatement instruction ('Denis also set aside the excavation and quarry for these — reinstate that too') — but no bedding/quarry-material cost line exists anywhere in the model for the 608.5 m of GT trench across both stages. Stage1A_Drainage's only bedding-stone formula (Q1) explicitly sums the pipe/DWV rows only and excludes the GT channel rows (G1/G2). | Unquantified — no cost line exists to measure against; a fresh, purpose-built estimate is required, not an inference from the pipe-trench bedding rate. | Add a GT-specific bedding/quarry material line (materials + contingency) to Stage1A_Drainage and Stage1B_Drainage before the draft is treated as satisfying the §5.3 locked instruction in full.
3 | HIGH | FT-04, FT-41, Equipment_Test row 1 | WSUD PC Sum (§9) | The $90,064.63 Reece Q-459014431 base rate for the 22-cartridge StormFilter manhole is the ONLY project-specific price on file and has not been reconciled against a direct Ocean Protect re-quote on the actual MUSIC model. An internal Ocean Protect-derived benchmark (18-cart $70,060 / 13-cart $60,460 → ≈$1,920/cartridge, ≈$35.5k base) implies ≈$77.7k pre-freight for 22 cartridges — roughly 16% below the Reece line. The PC sum this drives ($111,787.74) is a material, separately-disclosed figure in the submission. | ≈$12k gap on the PC-sum base rate (pre-freight, pre-15% markup) — disclosed range only, not a confirmed number; a live re-quote is the only way to close it. | Obtain the direct Ocean Protect re-quote (Gap #1/Opens #10) before the PC sum figure is locked for issue; this is already an open item and should be prioritised given its external visibility in the submission's own PC Sum table.
4 | HIGH | FT-26, Equipment_Test row 3 | Road gully inlets (§8.2) | The road gully inlet (RGU) supply rate — $1,350/ea across 33 units, $44,550 of materials value — is a benchmark carried forward from the old Civ workbook with an explicit internal note that no current RGU/lintel package quote exists ('sourcing gap'). This is the single largest precast-pit material line without a live 2026 quote. | $44,550 (materials, pre-contingency) resting on an unconfirmed rate. | Obtain a current RGU/lintel package quote before award; flag internally as a live re-quote item (already partially flagged on Materials_Master, but not yet resolved).
5 | HIGH | FT-40 | Stage 1B standalone viability (§8.4, Table 2) | The submission states Stage 1B 'is viable if awarded alone' (Table 2), and 1B does carry dedicated, separately-quantified establishment/testing/CCTV crew-day activities (not a bare percentage split) — but its Leading Hand supervision and accommodation/FIFO travel cost are both derived by a pro-rata crew-day ratio against the COMBINED 1A+1B base, not independently costed for a stand-alone 1B mobilisation. A genuinely stand-alone smaller award would plausibly need its own full FIFO/accommodation cycle, not a fractional share of a combined roster. No independent stand-alone-1B cost scenario exists in the model to test the claim against. | Not quantifiable without a fresh, independently-built stand-alone 1B cost run. | Obtain or build an independently-costed stand-alone Stage 1B scenario (its own LH-day allocation and its own accommodation/FIFO sizing) before repeating the 'viable if awarded alone' claim unqualified, or soften the wording to acknowledge the apportionment method used.
6 | MEDIUM | FT-29, FT-30, RT-04, Equipment_Test rows 1-2 | Heavy plant allowances (§8.2) | 50t mobile crane (8d, $30,400), franna/pick-and-carry (17d, $37,400) and trench shields (14d, $1,680) — $69,480 combined pre-markup — are all carried as internal day-rate ALLOWANCES explicitly flagged 'not in hire registers' on Equip_Master. The activities are correctly claimed as included and the cost exists, but the rates rest on no confirmed supplier quote. | $69,480 pre-markup (materiality of the rate-confirmation risk, not a missing-cost figure — the cost itself is present). | Obtain firm hire-house quotes for 50t crane, franna and trench shield hire before award; the current allowance rates should be treated as provisional.
7 | MEDIUM | FT-07, FT-17 | Compaction/testing standard (§7.3) | The compaction standard (98% Modified MDD) is priced 'in accordance with the specification tables' without naming which specification. VOL 38 (hydraulic spec, present) §3.62 is the only compaction table on file; VOL 35 — the actual governing civil specification — is absent. Per the document-wide confidence ceiling (RUN_STATUS/D6 register §12 rule), an inclusion whose compliance basis rests on an unseen civil-spec clause cannot be rated High confidence, and a borrowed hydraulic-spec table should not silently stand in for the missing civil spec. | Not quantifiable — a compliance-basis risk, not a missing cost. | Name the specification basis explicitly in §7.3 (VOL 38 §3.62 borrowed by analogy, pending VOL 35), and treat as Medium confidence until VOL 35 is sighted or CMDG is confirmed as the sole controlling document for civil compaction.
8 | MEDIUM | RT-07 | Prelims cross-check surplus (§5.4 methodology) | The bottom-up true-preliminaries figure ($62,561.25) sits $49,185.78 (44.0%) BELOW the 5.5% allowance actually carried in the sell ($111,747.03). Tested specifically per instruction: every bottom-up line traces to a Noted-Inclusions sentence, so the surplus is not concealing an unpriced obligation. It functions as additional, undisclosed margin sitting inside the 'prelims' label rather than the 'profit' label. This is the opposite finding to the TPS package (which ran a genuine $19,628 prelim SHORTFALL) and is not itself a Rule 4 defect, but is a pricing-discipline/labelling item. | $49,185.78 (cost basis) — not a missing-cost exposure, a margin-labelling observation. | Director to decide whether the surplus should be retained as a VOL-35-driven risk buffer (defensible, given the confidence ceiling elsewhere in this report) or re-labelled/reallocated for internal governance clarity. No external wording change is required.
9 | MEDIUM | FT-38, Equipment_Test row 4 | GT6 grate substitution | GT6 (Stage 1B, amenities building) is priced on a Reece-offered PRO200 G-tec ductile-iron grate, while the F1320 schedule specifies PRO100 D400 code 47245 — a different product. Register Gap #7 flags this internally as unverified. Value at risk if the substitution is rejected: the full GT6 material line. | $12,171.53 (GT6 material line, pre-markup) at risk of a spec-mismatch rebuild if the substitution is not accepted. | Confirm equivalence with Reece or obtain a compliant-product quote before order; not a submission blocker but should be resolved before Director sign-off on the rate.
10 | LOW | (Quote Register Notes §1 P07) | Hauraton Fibretec rate anomaly | An embedded annotation in the Reece quote shows an alternative $198.00/m rate against the tendered $232.94/m rate on the 550 m Fibretec channel line — a $19,217 delta. The model has conservatively adopted the HIGHER ($232.94/m) rate, so this is a possible pricing upside/negotiation opportunity, not a downside risk to the tendered sum. | $19,217 potential favourable delta (not an exposure — the tendered price is already the conservative figure). | Confirm with Reece which rate is correct before order placement; no action needed before submission since the model is already priced conservatively.
11 | LOW | FT-20, FT-25, Query B1 | C09A/B twin-culvert headwalls | The twin 2×375 RCP crossing at C09A/B is detailed nowhere in the issued drawing set (no headwall, apron or rock-pad detail); the submission prices 2 standard precast headwalls ($1,177.60) and explicitly qualifies that non-standard structures are unpriced (Query B1). Correctly disclosed, low materiality. | $1,177.60 (materials only) at risk if the structure proves non-standard — low materiality. | No action required before submission — already correctly qualified; close via Query B1 response before construction.
12 | LOW | Equipment_Test row 1 | WSUD unit-specific testing | General §7.3 'testing and flushing of the included drainage' is the only testing/commissioning coverage named for the WSUD filtration unit; no filtration-specific test/commissioning line is named separately. | Not quantifiable — likely functionally covered, just not explicitly named. | Consider adding one sentence in §9 or §8.2 naming WSUD-specific testing/commissioning if the Director wants this made explicit; low priority.