Stanwell Power Station — New Office Building & Annex

Hydraulic Services Tender Proposal

BUDGET QUOTATION

Stanwell Power Station — New Office Building & Annex Refurbishment

Hydraulic Services

| Date | Saturday 13 June, 2026 | Quote # | 2381 |
| --- | --- | --- | --- |
| Prepared For | Estimator | Attention | Estimator |
| Project | Stanwell Power Station — SPS New Project Building (Scope A) & SPS Annex Refurbishment and Build (Scope B) |  |  |
| Site Address | 397 Power Station Road, Stanwell QLD 4702 | Validity | 30 days from proposal date |
| Tender Basis | Lump Sum construct-only — subject to clarifications herein |  |  |
| Submission Type | Hydraulic Services Tender Proposal |  |  |

Dear Estimator,

Please find enclosed our tender proposal for the above-mentioned project. This quotation is based on receipt and review of the issued documentation, drawings, project specification, architectural interface information and project correspondence relevant to the hydraulic services scope.

# Tender Value

| Description | Basis | Amount |
| --- | --- | --- |
| Scope A — SPS New Project Building | Excluding GST | $562,394.51 |
| Scope B — Annex Refurbishment and Build | Excluding GST | $598,336.25 |
| Tender Value | Excluding GST | $1,160,730.76 |
| GST | 10% | $116,073.08 |
| Tender Value | Including GST | $1,276,803.83 |

# Description of Proposed Services and Scope of Works

Supply and installation of complete hydraulic services on a construct-only basis, comprising: sanitary plumbing and drainage; cold and hot water reticulation; roof / stormwater drainage reticulated suspended to structure and extended to civil connection points; fire hydrant service including new dual pillar hydrant to AS 2419.1 and connection / upsizing of the existing hydrant service to 100Ø (existing fire main 200 DICL per Q33); hose reels; backflow prevention (incl. testable RPZD-25 to irrigation supply); fixtures and tapware per the fixture register; testing, commissioning and certification including authority inspections (Pay Table A2.11.01–.09, A2.13.05).

# Drawing and Documentation Packages

- Scope A: JHA Q250128 hydraulic set H0000–H9000 (Rev B–H, 'Issue for Council Approval' 14.01.2026), incl. Form 15 design certification (AS 3500.3:2021) and box-gutter performance solution; architectural T-Sheets and wet area details.

- Scope B: 690a Main Warehouse, 690b New Building (incl. H.03.02 v03 minor change), 690c Registry, 690d Workshop hydraulic tender plans; Annex architectural sets A0–A4.

- SOW (A) and SOW (B) Rev A; geotechnical RG25-1156A and Annex geotechnical report; service location and survey documentation; project correspondence and clarifications to date.

# Work Area Pricing Summary

| Code / Work Area | Pay Table Ref | Amount ex GST |
| --- | --- | --- |
| Scope A — SPS New Project Building (in-ground site services, suspended stormwater ring, fixtures & equipment) | A2.11.01–.09 | $562,394.51 |
| Scope B — New Office Building (A4 New Build) | SOW (B) | $298,228.25 |
| Scope B — Workshop (refurbishment) | SOW (B) | $113,493.05 |
| Scope B — Registry (refurbishment) | SOW (B) | $94,955.41 |
| Scope B — Main Warehouse Office (refurbishment) | SOW (B) | $91,659.54 |
| Hydraulic Services Tender Value (ex GST) |  | $1,160,730.76 |

# Construct-Only / Documentation Basis

This tender is construct-only. No design services, design development or professional indemnity for design are included. The works will be constructed to the issued, certified documentation (Form 15 to AS 3500.3:2021 for the Scope A drainage design). Design changes, performance solutions or re-certification arising after tender are variations.

# Noted Inclusions

- In-ground excavation, bedding and backfill for hydraulic services self-performed by TriCore, including site water, fire and sewer connections (sewer point of connection located post-pothole as documented).

- Fire hydrant service: new dual pillar hydrant (AS 2419.1, no prescribed product per Q34), upsize of existing hydrant service to 100Ø, tie-ins to existing 200 DICL main; hose reels.

- Hot water units: 7 units priced (3× DHB-E18 male/female/first-aid areas, 2× DHB-E18 PWD/shower, 1× DHB-E13 covered outdoor area, 1× DHB-E18 kitchen underbench).

- Filtered water units: 1× HydroTap G5 BC100 Classic Accessible (kitchen); 3× HydroTap G5 BCHA20 4-in-1 Classic (boardroom, kitchen, health).

- Refurbishment buildings: isolation of services for demolition; removal / strip-out of all redundant plumbing; setout and coordination of demolition works.

- Testing, commissioning, certification and authority inspections; temporary plumbing connections as scheduled.

# Building-Specific Scope Clarifications

- Q11 — urinal selections per corrected schedule; fixtures priced per the issued fixture register (37 fixtures / 76 fixture units per H0003 Fixture Unit Table for Scope A).

- Hot water unit quantity: the architectural schedule indicates a count exceeding the hydraulic drawing schedule's service areas; this tender carries 7 physical units across the 4 scheduled service areas. Variance to be ratified by clarification.

- Q31 — 100 grated drain detail remains pending from the hydraulic consultant; carried as a named allowance until the detail is issued.

- Q33/Q34 — existing fire main 200 DICL; dual pillar hydrant to AS 2419.1 with no prescribed manufacturer.

# Provisional Sums and Tender Allowances Included

- Hydraulic Services Diversion — aligned to Pay Table PS1.0.15 (as scheduled in the returnable).

- Q31 grated drain allowance — named allowance pending issued detail.

- Cold water meters — provisional sum to each building.

- Concrete cutting & penetration Provisional Sums per refurbishment building (basis: 6 lm saw cutting and 3 hrs tradesman labour per proposed fixture shown on plan; maximum existing slab depth 100mm; excludes removal and disposal of cut material, by others): Main Warehouse Office $2,130.00 (3 fixtures); Registry $2,800.00 (4 fixtures); Workshop $3,470.00 (5 fixtures). Fixture counts to be ratified against final plan counts.

# Demolition, Isolation and Access Basis

Demolition and builder's works (including concrete cutting and removal beyond the Provisional Sums above) are by others. TriCore includes isolation of live services for demolition, strip-out of redundant plumbing, and setout / coordination attendance on demolition as noted in Inclusions. Access assumed progressive and unimpeded per the head contractor's program.

# Exclusions / Notes

- Civil stormwater beyond building connection points (refer TriCore Civil Stormwater proposal 2380).

- Demolition, concrete cutting and removal (other than the Provisional Sums offered).

- Electrical fire and dry-fire systems are excluded, including FIP/FDCIE/EWIS, detectors, MCPs, WIPs, speakers, bells, VADs, ASD, fibre, networking, fire alarm cabling, terminations, programming and cause/effect.

- Portable extinguishers, fire blankets, portable signage and all sprinkler systems are excluded, including sprinkler pipework, heads, valves, tank-fill controls and sprinkler controls.

- Existing services locating, protection, support, relocation, impact management, diversions, unknown depths/levels and works arising from undocumented service clashes are excluded unless specifically scheduled as a named allowance.

- Vacuum excavation is excluded.

- Site-wide water, sewer, stormwater or fire system testing, reconfiguration, augmentation or authority-driven upgrade beyond the documented scope and named allowances is excluded.

- AMR/BMS/electronic/smart metering systems, meter head-end/software, BMS graphics, programming, trending, alarming and integration are excluded beyond local equipment terminals/contacts where included.

- Cold water meters are carried to each building only as a provisional sum. AMR/metering system components are excluded.

- Development of coordinated multidisciplinary penetration plans is excluded. Hydraulic penetration inputs, sizes and mark-ups for our scope are included.

- Slab scanning/x-ray, structural approvals for coring and remedial works arising from concealed structural/services conditions are excluded. Core hole cutting allowance is included only as scheduled.

- Drainage articulation is included as swivel/expansion entering the building footprint only. Strapping to slab and expansion treatment to every riser are excluded unless later directed and priced.

- Builder's works in connection, architectural openings, access panels, hatches, cupboards/recesses, plinths, slabs, bollards, plant screens, roof works, gutters, downpipes and waterproof membranes are excluded unless specifically noted as included.

- Contaminated material, asbestos, PASS, rock, unsuitable material, heavy groundwater/dewatering and any associated treatment/disposal/replacement costs are excluded.

- Traffic and pedestrian management, permits, paid parking, security escorts and stakeholder access controls are excluded unless expressly noted as included.

- Third-party surveyor engagement for set-out, ADAC or survey-as-constructed documentation is excluded unless expressly stated otherwise.

- Supply of temporary fixtures, fountains, pumps, tanks or temporary appliances is excluded. Temporary service allowance is limited to typical connection material only.

- Any post-tender scope growth, redesign of other disciplines, changes arising from final room layouts, equipment changes, authority comments, certifier requirements or undocumented existing conditions are excluded unless instructed and valued as a variation or covered by a named provisional sum.

# Conditions

- Title of all works, including consumables, remains the property of TriCore Plumbing Services Pty Ltd until payment has been received in full.

- Prices are based on completion of works in a logical sequence with reasonable clear access and coordinated work fronts provided by the builder.

- Due to supply/manufacturer price securement and procurement requirements, reasonable claim may be made for major project materials procured and delivered to site or otherwise secured for the project.

- Extension of time and associated costs may apply for wet weather, latent conditions, design changes, authority changes, restricted access, shutdown constraints, public holidays, Christmas shutdown, third-party interruption or circumstances outside TriCore control.

We invite you to please contact our office or myself should you require further information regarding this quotation.

Sincerely,

Mitch Hannan

__________________

Mitch Hannan

TRICORE PLUMBING SERVICES PTY LTD

ABN 89 620 147 935

PO Box 7081 Hemmant Q 4174

Tel. 07 3390 5803

Tricoreplumbing.com.au

# Appendix A — Hydraulic Fixture and Equipment Register

Scope A — SPS New Project Building (per Q250128 H0003 Fixture Unit Table). Refurbishment and Annex building fixtures are priced within the respective work area values. Fixture units calculated for hydraulic calc and authority purposes.

| Qty | Fixture / Equipment | FU | Notes |
| --- | --- | --- | --- |
| 10 | WC suite | 40 |  |
| 9 | Wash basin | 9 |  |
| 8 | Sink | 24 |  |
| 3 | Tundish / floor drain | — |  |
| 1 | Shower | 2 |  |
| 1 | Urinal | 1 |  |
| 1 | Testable backflow RPZD-25 | — |  |
| 7 | Hot water units (Stiebel Eltron DHB-E) | — |  |
| 1 | HydroTap G5 BC100 Classic Accessible | — |  |
| 3 | HydroTap G5 BCHA20 4-in-1 Classic | — |  |
| 37 | Total fixtures | 76 |  |