## TCS_Civil
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
PIPELINES (Rule 2: printed long-section chainages govern where Groundplan exceeds them)
100 PVC DWV SN8 (subsoil outlets / building DP laterals) | m | 283.71 | n/a | No printed design total exists for 100 dia (layouts F1300-F1305 graphical only) | 0 | No independent total available | 283.71 | M | Accepted as measured (legends p1/p3/p4). Shown as subsoil outlets @600 cover + DP laterals.
150 PVC DWV SN8 | m | 62.85 | 62 | F1350-F1363 long sections - trash-box laterals lines 30-53/60/61/83/87 | 0 | Within tolerance (+0.9 m / +1.4%) | 62.85 | H | Steep laterals to 29.21% grade; connects Hauraton trash boxes.
225 PVC DWV SN8 (line 81, building drainage collector) | m | 180.93 | 115.45 | F1360/F1361 line 81 printed chainages (115.447 m) | -65.48 | Continuation-line double-measure (printed design data governs) | 115.45 | M | Denis's extra ~65.5 m unidentified (possibly building cut-off drains / bi-fold outlets measured as 225) - Opens #1. Adopted printed line-81 total per Rule 2.
RCP 375 CL3 (incl. C09 twin barrels 12.03 m) | m | 695.07 | 702.9 | F1350-F1363 run-by-run printed chainage sums (long-sections note derived totals) | 7.83 | Class re-split: part of Denis's 30.40 m CL4 belongs in CL3; lines 06/11 continuation overlap nets off | 702.9 | H | Combined 375 adopted 714.9 m vs Denis 725.47 m (-10.6 m). Rule 2's '~+35 m' traces to a mis-sum in the take-off note (design ~690.4 dropped line-06 start ch -24.498 = 24.5 m); printed run sums govern - Opens #3.
RCP 375 CL4 | m | 30.4 | 12 | F1350 line 05 (05-01 to 06-03, 11.988 m - only run printed CL4) | -18.4 | Only line 05 is printed CL4; Denis's CL4 extent unverified | 12 | M | Class split affects supply rate only; total 375 length held at 714.9 m - Opens #2.
RCP 600 CL3 (legend typo 'RPC') | m | 3.31 | 3.12 | F1355/F1356 line 26 (26-03 to 26-02) - 1 in 500 grade | 0 | Within tolerance (+0.19 m) | 3.31 | H | Netball court drainage outlet stub; tight laser control obligation at 0.20% grade.
225 PP (Denis: '225mm HDPE PN100 SN8') | m | 137.67 | 139 | Long sections lines 26/27/28/29 (~138.9-139.0 m) | 0 | Within tolerance (-1.3 m) | 137.67 | H | Drawings label PP - price as PP (StormPRO or equal), not HDPE PN100 (not a real class) - Opens #5.
300 PP | m | 58.56 | 61.3 | Long sections lines 25/29 (~61.3 m) | 0 | Within tolerance (-2.8 m / -4.6%) | 58.56 | H | Slightly under design; immaterial. Line 25 (tank line) is the deepest pipework on site (1.57-1.67 m).
375 PP | m | 210.43 | 201.8 | Long sections lines 27/28/29 (3 x ~67.25 m collectors) | 0 | +8.7 m (+4.3%) probable sheet-continuation over-measure; Denis retained (H002 n.15 larger-quantity regime) | 210.43 | M | Not in Rule 2's named overage list - retained conservatively.
450 PP | m | 41.47 | 42.3 | F1356 line 26 (26-06/26-07/26-08) | 0 | Within tolerance (-0.8 m) | 41.47 | H
600 PP | m | 38.47 | 38.7 | F1356 line 26 (26-04/26-05) | 0 | Within tolerance (-0.2 m) | 38.47 | H
CULVERTS (all verified vs F1362/F1363 printed lengths within 0.3 m)
RCBC 600x300 (C05-C08) | m | 33.39 | 33.12 | F1362 (6.851 + 8.565 + 8.000 + 9.708) | 0 | Within tolerance (+0.27 m) | 33.39 | H | Zero/negative cover at headwalls - excavation/bedding extra-over in NewItems #2.
RCBC 750x300 (26-01 to 26-02, WSUD high-flow bypass) | m | 5.17 | 5.24 | F1355/F1356 line 26 (5.241 m) | 0 | Within tolerance (-0.07 m) | 5.17 | H
RCBC 900x450 (C01, C02) | m | 27.86 | 28 | F1362 (22.996 + 5.000) | 0 | Within tolerance (-0.14 m) | 27.86 | H
RCBC 1200x600 (C03) | m | 17.77 | 17.7 | F1362 (17.700 m) | 0 | Within tolerance (+0.07 m) | 17.77 | H
RCBC 1500x600 (C04) | m | 29.04 | 29.15 | F1362 (29.148 m) | 0 | Within tolerance (-0.11 m) | 29.04 | H | Cover over obvert only ~0.17/0.37 m at headwalls.
RCBC 2700x1200 (C10, basin controlled-discharge outlet) | m | 17.53 | 17.28 | F1363 (17.276 m) | 0 | Within tolerance (+0.25 m) | 17.53 | H | Heavy lift; ~0.11-0.15 m cover at headwalls; embankment over mid-length (height not annotated).
SUBSOIL DRAINAGE (record only - scope excluded)
Subsoil / type 2 strip filter drain (100 dia) | m | 2172.4 | n/a | No schedule exists (CMDG-D-040/041, IPWEA RSD-802 details only) | 0 | No independent total available | 2172.4 | M | RECORD ONLY - EXCLUDED 'by others' per SCOPE_MATRIX 2.3-x2 / 2.5-x3 (locked 5.3); interface = TCS collector-pit wall penetration; Design Report re-shape to type 2 strip filters qualified (CL F5).
GRATED TRENCH DRAINS (Rule 2: F1320 schedule 608.5 m adopted; GT1-GT4 overage = sheet-continuation double-measure)
GT1 Recyfix Pro 200 B125 Fibretec (code 47246) | m | 128.73 | 125.2 | F1320 Grated Trench Schedule | -3.53 | Continuation-line double-measure (measured across F1300 + F1302) | 125.2 | H | Stage 1A (Sch 1A 3.5, TCS per locked 5.1).
GT2 Recyfix Pro 200 B125 Fibretec | m | 143.78 | 141.2 | F1320 schedule | -2.58 | Continuation-line double-measure (F1302 + F1303) | 141.2 | H | Schedule 'NO. PITS = 4' does not reconcile with layouts - RFI (Opens #7).
GT3 Recyfix Pro 200 B125 Fibretec | m | 145.42 | 141.2 | F1320 schedule | -4.22 | Continuation-line double-measure (F1302 + F1304) | 141.2 | H
GT4 Recyfix Pro 200 B125 Fibretec | m | 143.96 | 141.2 | F1320 schedule | -2.76 | Continuation-line double-measure (F1302 + F1304) | 141.2 | H
GT5 Recyfix Pro 100 B125 SS heelguard (47307) - multi-use court | m | 15.21 | 15.2 | F1320 schedule | -0.01 | Rounding | 15.2 | H | Stage 1B (2.3-a) per adopted stage basis (interface L10).
GT6 Recyfix Pro 200 D400 ductile (47245) - amenities bldg | m | 31.75 | 31.4 | F1320 schedule | -0.35 | Minor over-measure | 31.4 | H | Class D400 outlier (all others B125). Stage 1B.
GT7 Recyfix Pro 100 B125 - netball walkway | m | 3.58 | 3.6 | F1320 schedule | 0.02 | Rounding | 3.6 | H
GT8 Recyfix Pro 100 B125 - netball stairs | m | 6.01 | 6 | F1320 schedule | -0.01 | Rounding | 6 | H
GT9 Recyfix Pro 100 B125 - netball walkway | m | 3.65 | 3.5 | F1320 schedule | -0.15 | Minor over-measure | 3.5 | H
GT TOTAL (adopted basis Rule 2) | m | 622.09 | 608.5 | F1320 schedule sum (125.2+141.2x3+15.2+31.4+3.6+6.0+3.5) | -13.59 | Continuation-line double-measure concentrated on GT1-GT4 | 608.5 | H | ADOPTED = 608.5 m + 29 trash boxes (25 x TB200 + 4 x TB100) + 28 GT pits per schedule. Split: GT1-4 + GT7-9 = 561.9 m to 1A 3.5; GT5 + GT6 = 46.6 m to 1B 2.3-a.
ROCK PADS / EROSION PROTECTION (areas - no independent totals; F1321/F1325 dims allow Phase 6 check)
Kerb chute rock D100/180 thick + erosion control matting | m2 | 55.67 | n/a | F1325 kerb outlet detail (dims only, no schedule) | 0 | No independent total | 55.67 | M | Subject to Director decision D6-F1 (full exclusion vs rock+mat only) - both positions costed.
Culvert headwall rock D50=200, depth 360 | m2 | 70.4 | n/a | F1300/F1302 notes; F1321 pad dimension tables | 0 | No independent total | 70.4 | M | F1321 pad dims (e.g. C03 5.88x7.20) permit Phase 6 arithmetic check.
Culvert headwall rock d50=100, 180 thick | m2 | 179.56 | n/a | F1321/F1325 details | 0 | No independent total | 179.56 | M
Basin rock D50=500, depth 900 (C10 inlet+outlet) | m2 | 263.33 | n/a | F1305 basin rock pad notes | 0 | No independent total | 263.33 | M
FITTINGS / IN-LINE ITEMS (legend counts - no independent source)
100 PVC 90 deg bend | EA | 17 | n/a | Legends p1/p4 | 0 | - | 17 | M
100 PVC 45 deg bend | EA | 9 | n/a | Legends p1/p4 | 0 | - | 9 | M
225 PVC 90 deg bend | EA | 1 | n/a | Legend p4 | 0 | - | 1 | M
100 PVC 45 deg junction | EA | 26 | n/a | Legends p1/p3/p4 | 0 | - | 26 | M
225 PVC 45 deg junction | EA | 1 | n/a | Legend p4 | 0 | - | 1 | M
225x100 PVC 45 deg junction | EA | 11 | n/a | Legend p4 | 0 | - | 11 | M
Inspection opening, galvanised cover flush with surface | EA | 3 | n/a | Legend p4 (F1303 'IO flush with surface (TYP.)') | 0 | - | 3 | M
STRUCTURES (Rule 3: adopt F1310 121 unique + 20 C-series end structures = 141)
Headwall to suit 375 RCP | EA | 5 | 5 | F1310 (01-01, 10-01, 11-01, 12-01, 19-01) | 0 | Match | 5 | H | Precast headwall with inlet screen.
Headwall to suit 2x375 RCP (C09A/C09B) | EA | 2 | 2 | F1362/F1363 + F1304 layout | 0 | Match | 2 | M | Details in NEITHER F1310 nor F1321; both ends labelled 'HEADWALL OUTLET'; C09B IL above C09A - RFI (Opens #8).
Headwall to suit 150 PVC (87-01) | EA | 1 | 1 | F1310 | 0 | Match | 1 | H
Headwall to suit 225 PVC | EA | 2 | 1 | F1310 (81-01 only) | -1 | Schedule basis - only 81-01 exists; Denis's second symbol unmatched | 1 | H
Headwall to suit 300 PP (25-01) | EA | 1 | 1 | F1310 | 0 | Match | 1 | H
Headwall to suit RCBC 600x300 (C05A/B-C08A/B) | EA | 8 | 8 | F1321 Table 1 + layouts | 0 | Match | 8 | H
Headwall to suit RCBC 750x300 (26-01) | EA | 1 | 1 | F1310 | 0 | Match | 1 | H
Headwall to suit RCBC 900x450 (C01A/B, C02A/B) | EA | 4 | 4 | F1321 Table 1 | 0 | Match | 4 | H
Headwall to suit RCBC 1200x600 (C03A/B) | EA | 2 | 2 | F1321 Table 1 | 0 | Match | 2 | H
Headwall to suit RCBC 1500x600 (C04A/B) | EA | 2 | 2 | F1321 Table 2 (TMR SD1250, C04A skew 22 deg) | 0 | Match | 2 | H
Headwall to suit RCBC 2700x1200 (C10A/B) | EA | 2 | 2 | F1321 Table 2 | 0 | Match | 2 | H
Inlet (on-grade, 2.4 m RGU) CMDG-D-020 | EA | 28 | 28 | F1310 | 0 | Match | 28 | H
Inlet (sag, 2.4 m RGU) | EA | 5 | 5 | F1310 | 0 | Match | 5 | H
1050 access chamber CMDG-D-030 | EA | 13 | 13 | F1310 | 0 | Match | 13 | H
1200 access chamber | EA | 3 | 4 | F1310 (25-03, 26-02, 26-03, 26-05) | 1 | Schedule governs - Denis -1 (which one missed not identified) | 4 | H | Opens #4. 26-02 carries the 0.467 m internal upstand (tank outlet control).
600x600 field inlet Type 2 CMDG-D-022 | EA | 3 | 3 | F1310 (81-02, 81-07, 87-02) | 0 | Match | 3 | H | 87-02 duplicated in schedule; long section labels '81-08' vs schedule 81-07 - RFI (Opens #9).
Pipe-to-pipe connection (all types) | EA | 19 | 20 | F1310 (20 P2P) | 1 | Schedule governs - Denis -1 (60-02 or 81-04 uncounted) | 20 | H | Opens #4. Denis's 'P2P (375 RPC, 100 PVC)' matches no schedule P2P.
WSUD treatment tank 25-02 (DN3300 manhole, 22 StormFilter cartridges) | EA | 1 | 1 | F1310 (25-02 TANK) + F1324 | 0 | Match | 1 | H | Cartridges/internals supply+delivery = PC Sum +15%; install in TCS lump sum (interface L3); Ocean Protect re-quote - Opens #10. Tank founding depth not shown (deepest excavation risk, refusal band).
Hauraton Trash Box 200 | EA | 25 | 25 | F1310 | 0 | Match | 25 | H | Part of Rule 2 GT adopted basis (608.5 m + 29 boxes).
Hauraton Trash Box 100 | EA | 4 | 4 | F1310 (60-01, 60-03, 61-01, 83-01) | 0 | Match | 4 | H
Kerb chute (structure: concrete invert, kerb returns, R1000) | EA | - (not counted) | 9 | F1310 (03-02, 03-03, 04-02, 13-02 to 18-02) + F1325 detail | +9 (new) | Never counted as EA - only rock/matting area measured (55.67 m2) | 9 | H (count) | Director decision D6-F1 pending (excluded vs rock+mat) - do not close either way; both positions costed in EBC register.
TOTAL STRUCTURES | EA | 131 | 141 | F1310 121 unique (122 rows less 87-02 duplicate) + 20 C-series end structures (F1362/F1363) | 10 | Rule 3 adoption: item-level deltas 1200AC +1, P2P +1, 225 headwall -1, kerb chutes +9 | 141 | H | F1310 defects (duplicate row, remarks shifted one row for 5 pits) noted - RFI (Opens #9).

## TPS_Site
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
MEASURED LENGTHS (Rule 1: vector-verified = Denis's legend, within 0.01 m; scale proven exact vs 30.5 m netball courts)
Ø200 Kembla copper Type B main (tapping to meter slab) | m | 134.63 | 134.63 | H003 25015-H003 T1 - independent PDF vector re-measure @1:500 | 0 | Vector-verified 0.00 m | 134.63 | H | Length firm. Locked 5.5 base offer = Ø200 ID HDPE PE100 SDR11 - re-rate material at Phase 6 (Opens #12).
125 PE100 PN16 blue stripe (site CW spine, 8 runs) | m | 236.88 | 236.88 | H003 vector re-measure | 0 | Vector-verified 0.00 m | 236.88 | H | Drawing labels Ø100 CW - 125 OD PE is correct DN100 substitution; 12 MaxiStubs = 6 flanged valve sets.
125 HDPE PN16 SDR11 REDLINE fire main (3 runs) | m | 217.73 | 217.72 | H003 vector re-measure | 0 | Vector-verified 0.01 m | 217.73 | H | Fire extent qualification (CL C1/F3): looks light vs AS2419.1; H004 continuation missing - Opens #13.
32 PE100 PN16 blue stripe (5 runs) | m | 37.26 | 37.26 | H003 vector re-measure | 0 | Vector-verified 0.00 m | 37.26 | H | Base drawing labels Ø25 - Denis upsized one size; convention retained per Rule 1 (Opens #11).
25 PE100 PN16 blue stripe (5 runs) | m | 74.25 | 74.25 | H003 vector re-measure | 0 | Vector-verified 0.00 m | 74.25 | H | Base drawing labels Ø20 - upsized one size; no Ø20 item exists in take-off.
DWV PVC 150 SN6 sewer (authority connection leg) | m | 29.29 | 29.29 | H003 vector re-measure (single run, MH-1 to property connection IL 35.433) | 0 | Vector-verified 0.00 m | 29.29 | H
DWV PVC 100 SN6 gravity sewer (7 runs @1:60) | m | 178.24 | 178.24 | H003 vector re-measure - runs pairwise-verified vs base sanitary lines | 0 | Vector-verified 0.00 m | 178.24 | H
Geberit HDPE 110 trade waste (clubhouse/canteen run) | m | 16.28 | 16.28 | H003 vector re-measure | 0 | Vector-verified 0.00 m | 16.28 | H
DWV PVC 225 SN8 storm connection stubs (10 stubs 0.49-0.98 m) | m | 6.91 | 6.91 | H003 vector re-measure | 0 | Vector-verified 0.00 m | 6.91 | H | Scope note: the long PVC-U 225 storm RUNS are TCS (civil line 81, interface L2) - stubs only here; pairs with 10 x 225 bends.
WATER - CONNECTION / TAPPING CLUSTER (counts)
200 SS gasket kit EPDM DI-DI | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
200mm copper tee | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
200mm copper 90 deg bend | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
200mm x 8in full-faced stub + SS backing ring AS4087 | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
200 FL DICL sluice valve | EA | 3 | 3 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 3 | H
200mm copper connection point (authority Ø300 MPVC main) | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
100mm fire water meter assembly + 100mm CW assembly (single legend item) | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H | Price as TWO assemblies under one item (legend groups both as 1 EA).
WATER - CW SPINE TAKE-OFF SETS + PE FITTINGS (counts)
100 FL DICL sluice valve | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
100mm check valve | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
100 SS gasket kit EPDM DI-DI | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
100mm PE*DI gasket kit complete | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
125PE x 4in (100mm) MaxiStub w/ backing ring | EA | 12 | 12 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 12 | H
HDPE 125 x 90 deg elbow | EA | 5 | 5 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 5 | H
HDPE 125 x 45 deg elbow | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
125mm EF tee | EA | 8 | 8 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 8 | H
125 x 32 reducing tee | EA | 3 | 3 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 3 | H
125 x 25 reducing tee | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
25mm tee | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
HDPE 32 x 90 deg elbow | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
HDPE 25 x 90 deg elbow | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
125 x 32 reducing coupler | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
32 x 25 reducing coupler | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
Hose tap (vandal-proof garden tap) | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
25mm isolation valve | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
25mm water cap | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
32mm water cap | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
FIRE MAIN (counts)
125 EF 45 deg bend | EA | 3 | 3 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 3 | H
125 EF 90 deg bend | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
125 EF coupler | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
125 EF tee | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
125 PE x 100 galv adapter (Plasson) | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
150mm H-pattern booster assembly complete | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
Booster cabinet complete w/ doors + stickers | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H
100mm dual pillar hydrant complete, flanged base 1500 high | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H | Only hydrant on the whole site take-off - coverage RFI (Opens #13).
SEWER + STORM (counts)
Material for 150mm sewer property connection | EA | 1 | 1 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 1 | H | At existing MH, IL 35.433.
Sewer maintenance shaft (SMS-1, SMS-2) | EA | 2 | 2 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 2 | H
DWV bend 100 x 90 deg | EA | 3 | 3 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 3 | H
DWV bend 100 x 45 deg | EA | 6 | 6 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 6 | H
DWV bend 225 x 90 deg F&F plain (storm stubs) | EA | 10 | 10 | H003 Groundplan auto-legend; key symbols visually confirmed in place | 0 | Auto-legend authoritative (Rule 1) | 10 | H

## TPS_NBC
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
SANITARY DRAINAGE (sheets NBC-100/101/102, Sewer layer)
DWV PVC 100 SN6 sewer | m | 230.07 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 230.07 | M | Ø100 @1:60 per SD2; 187.38+23.63+19.06.
DWV PVC 50 SN8 | m | 12.68 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 12.68 | M
DWV PVC 40 SN8 | m | 25.61 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 25.61 | M
DWV bend 100x90 | EA | 75 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 75 | M
DWV bend 100x45 | EA | 66 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 66 | M
DWV junction 100x45 | EA | 80 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 80 | M
DWV bend 50x85 | EA | 7 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 7 | M
DWV bend 50x45 | EA | 8 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 8 | M
DWV junction 100x40 | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
DWV bend 40x90 | EA | 18 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 18 | M
DWV bend 40x45 | EA | 18 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 18 | M
DWV reducer 100x50 | EA | 3 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 3 | M
DWV reducer 100x40 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Inspection opening to surface 100 (sewer) | EA | 10 | ~11 | vol06_11 drawn label counts | 0 | Legend total accepted (no independent measure) | 10 | M | Drawn IOS labels 9+2 (+ several on 102 n/v) - consistent.
100mm ORG | EA | 1 | 1 | H-NBC-100 drawn (1 ORG) | 0 | Match | 1 | H
In-wall tundish (sewer) | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M | Mech condensate discharges to TPS tundishes - mech trade supplies drain.
100 exp/knuckle joint | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M | Articulation ALLOWANCE for H1 'P' site is additional - NewItems #12.
100 4-way riser (2x40)(2x50) | EA | 9 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 9 | M
100mm clear out | EA | 18 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 18 | M
Basket trap (floor waste, sewer layer) | EA | 12 | ~22 labels | vol06_11 BT label census (14+1+~7) | 0 | Legend total accepted (no independent measure) | 12 | M | Drawn BT labels ~22 incl. trade-waste zone + match-line duplicates - reconcile with floor-waste grate count at Phase 4 fixture recount (Opens #18); do NOT merge with water-layer 'basket trap' x2.
FWG | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
VENT (DWV portion; verticals NOT included - see NewItems #7)
DWV PVC 100 SN6 vent (horizontal plan runs) | m | 17.06 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 17.06 | M | Plan-view only; ~13+ vertical risers unmeasured - NewItems #7.
DWV PVC 50 SN8 vent | m | 0.7 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 0.7 | M
Vent bend 100x90 | EA | 12 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 12 | M
Vent bend 100x45 | EA | 6 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 6 | M
Vent junction 100x45 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Vent bend 50x85 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Vent reducer 100x50 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Vent IOS 100 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
TRADE WASTE (sheet NBC-102; incl. 1.98 m + 2 bends logged on Vent layer - merged, count once)
110 HDPE trade waste drain | m | 54.78 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 54.78 | M | 52.80 TW layer + 1.98 vent-layer stub (layer misclassification merged - Opens #25).
Trench drain (TW, coldroom entry) | m | 0.98 | 1 | H-NBC-102 drawn (1 TRD) | 0 | Match | 0.98 | H
110 HDPE 90 deg bend (TW) | EA | 8 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 8 | M
110 HDPE 45 deg (TW) | EA | 24 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 24 | M
Junction 110 HDPE x 45 deg | EA | 16 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 16 | M
Junction 110x50 45 deg | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
110 HDPE to 50 HDPE reducer | EA | 5 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5 | M
Geberit HDPE 50 pipe | m | 12.47 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 12.47 | M
Geberit bend 50x88.5 | EA | 9 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 9 | M
Geberit bend 50x45 | EA | 5 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5 | M
110 TW inspection opening / CO | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
DWV bend 50x85 (TW) | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Bucket trap / silt trap | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
In-wall tundish (TW) | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
Tundish | EA | 4 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 4 | M
Geberit 4-way riser 110x56 | EA | 6 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 6 | M
Geberit exp socket 110 | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
Geberit adj DT trap bottom HDPE 110 | EA | 6 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 6 | M
50mm RPZD | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M | Possible overlap with NBC-202 RPZD positions - verify (Opens #15).
100mm check valve (TW) | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Grease trap: 1500L Viking PanelTim in-ground GIT | EA | 1 | 1 | H-NBC-102 drawn (1 GIT) | 0 | Match | 1 | H | Size conflict: 1500L dwg / 2000L Design Report / Halgan 550-5000L spec - PC/allowance per CL B6 (Opens #24). No GIT install detail in volume.
WATER (sheets NBC-200/201/202) - WS2 spec: >DN22 = 316 SS press-fit; copper measured (price both ways per locked 5.5 / CL C9)
40 PE100 PN16 pipe | m | 27.78 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 27.78 | M
32 PE100 PN16 pipe | m | 21.31 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 21.31 | M
25 PE100 PN16 pipe | m | 15.45 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 15.45 | M
Copper tube Type B 32 | m | 17.86 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 17.86 | M | WS2 deviation - stainless conforming + copper alternate (Opens #17).
Copper tube Type B 25 | m | 112.72 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 112.72 | M | WS2 deviation - as above.
Copper tube Type B 20 | m | 19.88 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 19.88 | M | WS2 deviation - as above.
20 PEX pipe black (cold) | m | 157.82 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 157.82 | M | PEX <=DN22 conforms WS2.
20 PEX pipe red (hot) | m | 65.29 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 65.29 | M
HDPE elbow 40x90 | EA | 3 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 3 | M
HDPE elbow 32x90 | EA | 4 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 4 | M
HDPE elbow 25x90 | EA | 5 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5 | M
Isolation valve 32 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Isolation valve 20 | EA | 3 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 3 | M
B-press elbow 90 x 20 | EA | 16 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 16 | M
B-press elbow 90 x 25 | EA | 35 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 35 | M
B-press elbow 90 x 32 | EA | 3 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 3 | M
B-press equal tee 20 | EA | 5 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5 | M
B-press equal tee 25 | EA | 15 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 15 | M
B-press equal tee 32 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
B-press reducing tee 32x20 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
B-press reducing tee 32x25 | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
Poly-to-copper adapter 40x32 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
Poly-to-copper adapter 32x32 | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
PEX-Cu crimp adapter 32 | EA | 1 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
PEX-Cu crimp adapter 25 | EA | 14 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 14 | M
PEX-Cu crimp adapter 20 | EA | 5 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5 | M
PEX-20 elbow | EA | 104 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 104 | M
PEX-20 equal tee | EA | 66 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 66 | M
Thermostatic mixing valve (TMV) | EA | 10 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 10 | M | No TMV count/cabinet note found on NBC-200/201/202 in vol06_11 review - allow per warm-water groups + RFI (Opens #28).
Hose tap | EA | 4 | 5 | vol06_11: HT 4 (200) + 1 (201) + 2 (202); NBC-201 HT symbol has no legend row | 1 | Drawn-but-uncounted symbol on NBC-201 - adopt higher (H002 n.15) | 5 | M | Verify - Opens #15. Backflow: GE ZB007 VBs / vertical break / single check triple-requirement (CL C8).
FHR (fire hose reel) | EA | 1 | 1 | H-NBC-202 drawn | 0 | Match | 1 | H | Priced in 4.11-d; water supply source to FHR unconfirmed (CL C8/B8 context).
FB (fire blanket, kitchen) | EA | - (not counted) | 1 | H-NBC-202 drawn | +1 (new) | Drawn item never taken off | 1 | M | Matrix 4.11-d prices FHR x1 + FB x1.
FE fire extinguishers 2.5kg ABE (NBC) | EA | - (not counted) | 8 | vol06_11: FE 3 (200) + 1 (201) + 4 (202) | +8 (new) | Drawn with no trade allocation | 8 | M | EBC + RFI per CL B8 (VOL38 14.1 plumber prices vs note builder provides).
20mm RPZD | EA | 3 | 4 | NBC-202 shows RPZD symbols at ~4 positions (GIT washdown, canteen x2, binwash) | 1 | Possible 1 EA undercount - adopt higher (H002 n.15) | 4 | M | One position may be covered by another counted device - verify (Opens #15).
20mm check valve | EA | 4 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 4 | M
Basket trap (water charge/self-priming) | EA | 2 | n/a | NBC legends D/E/F/H/I/J (25015-H-NBC set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M | Different scope from sewer basket traps despite same name - do not merge.
Hot water pump (water layer big-ticket) | EA | 1 | 0 | vol06_11: 'Pumps: none shown' on any NBC sheet | 0 | Retained Denis (conservative); drawn evidence conflicts | 1 | L | Verify what was marked (possibly HWU circulating pump at MECH-01) - Opens #15.
Rheem HWU 315L electric storage (model 61331507) | EA | 3 | 2 | H-NBC-200 (1) + H-NBC-202 (1) = 2 drawn; only one Rheem callout legible per sheet | -1 | Take-off double-count across legend pages H+J (Rule 4) | 2 | M | ADOPT 2. Workbook's orphaned AC17 block carried qty 3 - correct to 2. 'Ø100 SD FOR HOT WATER UNITS' (plural) at Amenities M noted (CL C8 item 10). Install per H-NBC-301 detail incl. safe tray, SS plinth, seismic strap.
STORMWATER (markers only - no pipe measured in this set)
'Has already measured in civil sw' markers (DP/storm connection points) | EA | 9 | 19+ / 11 | NBC-103 roof DPs: 19+ per clubhouse-note reading; 11 roof callouts + 12 ground labels per vol06_11 | see NewItems | Markers are annotation, not quantity; drawn DP count exceeds markers | see NewItems #5 | L | DP in-ground connection stubs adopted at 19 EA in NewItems #5 (RFI on count). TPS stub scope ends at 'CONNECT TO CIVIL' (interface L2).

## TPS_PAM
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
SANITARY DRAINAGE (PAM-100 + 0.45 m pick-up on PAM-200)
DWV PVC 100 SN6 sewer | m | 61.16 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 61.16 | M | 60.71 (plan D) + 0.45 (plan F, HWU safe-tray waste zone) - single count, no double-up confirmed.
DWV PVC 50 SN8 | m | 6.93 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 6.93 | M
DWV bend 100x90 | EA | 21 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 21 | M
DWV bend 100x45 | EA | 21 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 21 | M
DWV junction 100x45 | EA | 22 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 22 | M
DWV bend 50x85 | EA | 4 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 4 | M
DWV bend 50x45 | EA | 2 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
DWV reducer 100x65 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
DWV reducer 100x50 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
100mm ORG | EA | 1 | 1 | H-PAM-100 drawn (1 ORG) | 0 | Match | 1 | H
In-wall tundish | EA | 2 | 2 | vol06_11: IWTD x1 + TD (HWS tray) x1 = 2 tundish-type | 0 | Match | 2 | M
100 exp/knuckle joint | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M | H1 'P' articulation allowance additional - NewItems #12.
100 4-way riser (2x40)(2x50) | EA | 2 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
100mm clear out | EA | 6 | 7 | PAM-100 text layer: 7 'CO' annotations along WC bank + PWD | 1 | Drawing shows 7 vs 6 counted - adopt higher (H002 n.15) | 7 | M | Delta = 1 x Ø100 CO - Denis verify (Opens #16).
FWG | EA | 3 | 4 | vol06_11: FWG x4 drawn on H-PAM-100 | 1 | Drawn 4 vs counted 3 - adopt higher (Rule 6 feed) | 4 | M
VENT (verticals NOT included - see NewItems #8)
DWV PVC 65 SN6 vent (horizontal plan run) | m | 1.93 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1.93 | M | Plan-view only; Ø65 VP riser to above roof unmeasured - NewItems #8.
DWV bend 65x90 (vent) | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
DWV bend 65x45 (vent) | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
WATER (PAM-200) - WS2 spec: >DN22 = 316 SS press-fit; copper measured (price both ways per locked 5.5 / CL C9)
40 PE100 PN16 blue stripe (inground CW entry) | m | 3.27 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 3.27 | M
Copper tube Type B 32 | m | 9.56 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 9.56 | M | WS2 deviation - stainless conforming + copper alternate (Opens #17).
Copper tube Type B 25 | m | 26.9 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 26.9 | M | WS2 deviation - as above.
Copper tube Type B 20 | m | 0.96 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 0.96 | M | Very short measure - position not pinpointed (Opens #16).
20 PEX pipe black (cold) | m | 18.86 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 18.86 | M
20 PEX pipe red (hot/warm) | m | 5.89 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 5.89 | M
B-press elbow 90 x 20 | EA | 2 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
B-press reducing coupling 25x20 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
B-press equal tee 32 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
B-press reducing tee 32x25 | EA | 2 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
B-press elbow 90 x 32 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
B-press elbow 90 x 25 | EA | 15 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 15 | M
B-press equal tee 25 | EA | 7 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 7 | M
32 poly to 32 copper B-press adapter | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
PEX-Cu crimp adapter 32 | EA | 2 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 2 | M
PEX-Cu crimp adapter 25 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
PEX-Cu crimp adapter 20 | EA | 1 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 1 | M
PEX-20 elbow | EA | 16 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 16 | M
PEX-20 equal tee | EA | 7 | n/a | PAM legends D/F (25015-H-PAM set T1) - no printed totals on drawings | 0 | Legend total accepted (no independent measure) | 7 | M
Hose tap HT/VP (vandal proof) | EA | 1 | 1 | H-PAM-200 drawn | 0 | Match | 1 | H
32mm domestic water meter (check-meter assembly) | EA | 1 | 1 | H-PAM-200 drawn ('DOEMSTIC' legend typo) | 0 | Match | 1 | H | Check meter to authority reqs; NO PRV vs NBC 500 kPa - RFI (CL C8). Boundary vs site primary metering = interface L8.
Thermostatic mixing valve (TMV) | EA | 1 | n/v | PAM-200 note: 'PROVIDE TMVs IN SS LOCKABLE CABINETS... (TYPICAL)' - plural, count unstated | 0 | 1 plausible for single-HWU block but symbols unresolvable | 1 | M | Verify + allow per warm-water groups - Opens #16.
Rheem HWU 50L electric storage (model 61305007) | EA | 1 | 1 | H-PAM-200 drawn (1) | 0 | Match | 1 | H | 3x3.6 kW, 240L FHD; safety tray + PTR per AS3500; install per PAM-301 detail.
FE fire extinguisher (PAM) | EA | - (not counted) | 1 | vol06_11: FE x1 drawn | +1 (new) | Drawn with no trade allocation | 1 | M | EBC + RFI per CL B8 (matrix 3.11-d).
STORMWATER (markers only)
'Has already measured in civil sw' markers (DP points) | EA | 2 | 4 | H-PAM-101: 4 x Ø100 DP roof callouts vs 2 markers/2 ground risers | see NewItems | Markers are annotation; drawn DPs exceed markers | see NewItems #6 | M | DP stub connections adopted at 4 EA in NewItems #6; no 'connect to civil' note on PAM sheets - connection point undefined (RFI, CL C8).
FIXTURES (not in this take-off - see Fixtures sheet)
PAM sanitary fixtures (~8 WC / 1 BSN / 1 CSK / 2 TR) | EA | - (not counted) | see Fixtures | H-PAM-100/200 annotations; FF&E VOL28 types | - | PAM fixture take-off never done | see Fixtures | - | Flagged per Rule 6 - adopted on Fixtures sheet.

## Fixtures
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
PART A - COUNTED ROOMS (Canteen/Kitchen AR-NBC-3002 + Unisex C/R.03 & C/R.04 AR-NBC-3005; 25 symbols verified twice)
H.PS-04 Kitchen double sink (Stoddart 2400x600) | EA | 1 | 1 | AR-NBC-3002 wash bay; FF&E VOL25 p12 | 0 | Match | 1 | H | Tapholes drilled onsite; FF&E has NO quantities (types only).
H.PS-03 Kitchen single sink | EA | 2 | 2 | AR-NBC-3002 (prep bay + canteen servery); H-NBC-102/202 SK x2 | 0 | Match | 2 | H
H.TT-05 Tapware spray rinse | EA | 3 | 3 | AR-NBC-3002 | 0 | Match | 3 | H
H.TT-06 Billi boiling/chilled unit (Quadra 4180) | EA | 1 | 1 | AR-NBC-3002; FF&E VOL25 p13 | 0 | Match | 1 | H | Unit SUPPLIED BY RCC - price install into benchtop + water/waste connection only.
H.IC Cleanout (counted rooms) | EA | 1 | 1 | AR-NBC-3002 | 0 | Match | 1 | H | Further H.IC labels in uncounted rooms - Part B.
H.DW-01 Floor waste grate (counted rooms) | EA | 5 | 6 | AR-NBC-3002 (4) + AR-NBC-3005 C/R.04 (1) + C/R.03 drawn-but-unmarked (1) | 1 | C/R.03 count stopped mid-room - mirror-identical to C/R.04 (verified 6x zoom) | 6 | H
HW-03 Knee-operated wash basin (kitchen) | EA | 1 | 1 | AR-NBC-3002; FF&E VOL25 p11 (with tempering valve) | 0 | Match | 1 | H
H.TT-01 Basin mixer (counted rooms) | EA | 2 | 2 | AR-NBC-3005 (C/R.03 + C/R.04 vanities) | 0 | Match | 2 | H
HW-01 Handwash basin vanity (counted rooms) | EA | 2 | 2 | AR-NBC-3005 | 0 | Match | 2 | H
WC-01 Toilet suite standard (counted rooms) | EA | 1 | 2 | AR-NBC-3005 - C/R.03 pan drawn with grab rails but unmarked | 1 | C/R.03 pan uncounted (count stopped mid-room) | 2 | H
H.DW-02 Floor trough (counted rooms) | EA | 2 | 2 | AR-NBC-3005 shower recesses | 0 | Match | 2 | H | Stormtech linear trough - lengths per room layouts.
H.TS Shower rose (counted rooms) | EA | 2 | 2 | AR-NBC-3005 | 0 | Match | 2 | H
H.TM-01 Shower mixer (counted rooms) | EA | 1 | 2 | AR-NBC-3005 - C/R.03 mixer drawn but unmarked | 1 | C/R.03 mixer uncounted | 2 | H
PART B - WHOLE-BUILDING NBC TOTALS (7 of 9 arch sheets NEVER counted - 'not finalised' per Denis; Rule 6: higher count adopted; Phase 4 recount + Tradelink 1066143 reconciliation MANDATORY before pricing)
WC pans NBC - all types (WC-01 std / WC-02 ambulant / WC-03 accessible) | EA | 1 | 21 | vol06_11 hydraulic label counts: WC 19+2 sanitary, ~21+2 water sheets; arch census indicative 15+ pans | +20 | Fixture take-off incomplete (2 of 9 sheets counted) - adopt drawn count per Rule 6 / H002 n.15 | 21 | L | Match-line duplication risk in label counts - Phase 4 architectural recount governs final.
Urinals NBC (WC-04 / UR, Amenities M) | EA | - (not counted) | 3 | vol06_11: UR x3 (H-NBC-100/200); 3 units on arch elevation E | +3 (new) | Never counted | 3 | M | Britex Regal UR per FF&E.
Basins NBC (BSN / HW-01 / HW-02) | EA | 3 | 14 | vol06_11: BSN 11+3 labels; arch census HW-01/02 across p6-p8 | +11 | Uncounted wet areas - adopt drawn count | 14 | L
Hand wash troughs NBC (HWT / HW-02 type) | EA | - (not counted) | 4 | vol06_11: HWT x4 (H-NBC-200) | +4 (new) | Never counted | 4 | M | Stoddart WB.VTH vanity trough type.
Wash troughs NBC (WT) | EA | - (not counted) | 4 | vol06_11: WT x4 (H-NBC-100) | +4 (new) | Never counted | 4 | M
Cleaners sink NBC (CSK / HW-04) | EA | - (not counted) | 1 | vol06_11: CSK x1 (H-NBC-100); FF&E HW-04 | +1 (new) | Never counted | 1 | H | Stoddart CS.01.450 + mop holder I.HM.
Showers NBC (H.TS roses) | EA | 2 | 10 | vol06_11: SHR 7+3 labels (sanitary), 7+2 (water); arch H.TS labels 5/10 on p6/p7 | +8 | Uncounted changerooms (5-cubicle banks) - adopt drawn count | 10 | L
Shower mixers NBC (H.TM-01 Enware Tempostop) | EA | 1 | 10 | Paired 1:1 with roses; arch H.TM labels p6 (4) + p7 (6) | +9 | Uncounted changerooms - adopt paired count | 10 | L | 30-sec timed flow, tempered <=45C - TMV commissioning obligation.
Floor wastes / basket wastes NBC building-wide | EA | 5 (fixture count) / 12 BT (drainage take-off) | 22 | vol06_11: BT labels 14+1+~7 incl. binwash/TW zone | n/a | Uncounted rooms + naming overlap - adopt drawn count as interim | 22 | L | Grates supply via Tradelink line; traps/drainage bodies already in TPS_NBC counts - Phase 4 must reconcile to avoid DOUBLE COUNT.
PWD accessible suite NBC (WC-03 + H.TM-02 + H.PB + grab rails) | suite | - (not counted) | 1 | AR-NBC-3009 (PWD); FF&E VOL25 (WC-03, H.TM-02, H.PB, A.GS etc.) | +1 (new) | Sheet never counted | 1 | M | Component list per FF&E; AS1428.1 compliance.
ODF hydration station / drinking fountains NBC | EA | 1 | 2 | vol06_11: 2 fountains (DF Ø20 CW + handicap DF); elevations tag ODF on 3 faces (2001 West; 2002 East + North) | +1 | Counted 1 station (3-bubbler); drawn fountains = 2 - adopt higher | 2 | M | Chilled (VOL25) vs non-chilled (VOL28) same SKU DFCF400 - RFI (CL C10); carried as calculated PC Sum (matrix 4.12-e). 1 station vs 3 bowls basis unresolved (Opens #21).
Z.HB hose bibs (Multipurpose room) | EA | - (not counted) | 2 | AR-NBC-3001: 2 apparent on plan (8 label occurrences) | +2 (new) | Never counted; code unconfirmed | 2 | L | Allowance - AR-NBC-0010 code list not held (Opens #20).
H.EW units (Cold room / Storage 2) | EA | - (not counted) | RFI | AR-NBC-3003/3009: H.EW labels x3 each | n/a | Code unconfirmed (possible electric water heaters - would conflict with 2-HWU adoption) | RFI | L | Do not price until AR-NBC-0010 decoded (Opens #20).
PAM FIXTURES (never counted by Denis - PAM note flags ~8 WC / 1 BSN / 1 CSK / 2 TR; adopted per Rule 6)
WC pans PAM (WC-05/06/07, stainless + in-wall cisterns) | EA | - (not counted) | 7-8 | vol06_11: WC x7 (6 cubicles + 1 PWD, consistent PAM-100/200); PAM note reads ~8 | +8 (new) | Count conflict 7 vs ~8 - adopt higher (Rule 6) | 8 | M | Stoddart TP3 s/s + FD.CI.IW.PRF in-wall cisterns - blockwork rough-in.
BSN PAM (PWD basin, H.PB Caroma Care 700) | EA | - (not counted) | 1 | vol06_11: BSN x1; FF&E VOL28 H.PB | +1 (new) | Never counted | 1 | H
Cleaners sink PAM (CSK/CLSK, HW-04) | EA | - (not counted) | 1 | vol06_11: CSK x1; FF&E VOL28 | +1 (new) | Never counted | 1 | H
TR x2 PAM (undefined label, fed Ø20 DCW, drains via FWG) | EA | - (not counted) | 2 | H-PAM-100/200 north wall grid C | +2 (new) | Never counted; label undefined in PAM-001 | 2 | L | Allowance - RFI fixture type (Opens #22).
HW-02 handwash trough 1800mm PAM (unisex toilet 01) | EA | - (not counted) | 1 | FF&E VOL28 p6 (1800mm, 2 hob taps) | +1 (new) | Never counted | 1 | M
H.TT-04 timed flow taps PAM | EA | - (not counted) | 2 | FF&E VOL28 p7 (2 hob taps on HW-02 trough) | +2 (new) | Never counted | 2 | M
HW-06 knee-operated basin PAM ('Kitchen') | EA | - (not counted) | RFI | FF&E VOL28 p6 - located 'Kitchen' but PAM has no kitchen room | n/a | Location anomaly (CL of FF&E note #5) | RFI | L | Verify against PAM floor plans before pricing.
GOVERNING NOTE
Tradelink quote 1066143/SP $252,694.77 ex GST reconciliation | - | 25 fixtures counted (3 of ~10 wet areas) | ~$252.7k quote | Tradelink 15/07/26, expires 13/08/26 | n/a | Quote cannot be reproduced from the take-off | Line-by-line reconciliation at Phase 4 | - | Fixture supply = separate PC line Tradelink +15% (locked 5.3, matrix 4.12-c/3.12-a); Rule 4 fixture test feeds off this sheet.

## NewItems
Item | Unit | Denis qty | Independent qty | Independent source (doc + sheet ref) | Variance (Adopted - Denis) | Variance reason | ADOPTED qty | Confidence (H/M/L) | Notes
ITEMS NEVER COUNTED BY DENIS (Rule 5) - each row carries an adopted qty or explicit allowance/RFI status
Ø100 sewer rising main (QMax pumpwell to discharge MH) + fittings | m | - (not measured) | 60-110 (base-linework estimate) | H003 base linework (no Groundplan trace - verified by colour-layer analysis); QCPS32VC/A02 | +110 (new) | The one genuine quantity gap in the site set | 110 | L | ADOPT 110 m allowance basis, PE100 pressure pipe. Status: Excluded-But-Costed per SCOPE_MATRIX 2.1-x2; RFI on discharge point (CL C4 - 'location to be confirmed'); wording must prevent builder deeming it included in 2.1-b.
Culvert excavation / bedding extra-over - 130.76 m RCBC (6 sizes) | item | - (not counted) | 130.76 m runs; cover data printed | F1362/F1363 long sections: C01-C03, C05-C08 zero/negative cover; C04 cover ~0.17/0.37 m; C10 depth 1.311-1.350 m + base | n/a | Denis's open question - never quantified | Price in Phase 6 from long-section cover data | - | CMDG-D-011 install; heavy lift C10 2700x1200; surface tie-in where units sit proud (RFI on load class already in CL D8).
Detention basin earthworks (shaping / embankment) | item | - (not counted) | annotation only | F1305: crest RL30.00, spillway RL29.70, max depth 2.25 m - no volumes anywhere | n/a | Annotation only, never quantified in any set | NOT quantified - ALLOCATION question: bulk earthworks vs TCS drainage 1A 2.5 - RFI + Director | - | Matrix 2.5-x4 currently assigns basin bulk shaping to earthworks trade; Director to confirm before close (Opens #26).
Concrete spillway weir | m | - (not counted) | 50 | F1305 note ('CONCRETE SPILLWAY 50 m WEIR LENGTH') + F1323 build-up (125mm 25MPa, SL72 central, 75mm Type 2.3 sub-base, 1.5 m aprons, 0.5 m keys) | +50 (new) | Annotation only - in no Groundplan set | 50 | M | Carried in TCS 2.5-b per matrix 2.5-x4; add to Phase 6 pricing; allocation confirmed with basin RFI.
NBC roof-DP in-ground connection stubs (to 'CONNECT TO CIVIL') | EA | 9 markers ('already measured in civil sw') | 19+ (NBC-103) / 11-12 (vol06_11) | H-NBC-103 roof DPs 19+ per clubhouse-note reading; vol06_11 reads 11 roof callouts / 12 ground labels | +10 | Civil-set markers < drawn DPs - stub scope at risk of being lost between trades | 19 | L | ADOPT drawing DP count (higher reading) per Rule 5; RFI to settle count (Opens #23). TPS owns stubs to the 'CONNECT TO CIVIL' point; TCS beyond (L2). Expansion provision <=6 m at DP connections (reactive soil note).
PAM roof-DP in-ground connection stubs | EA | 2 markers | 4 | H-PAM-101: 4 x Ø100 DP roof callouts vs 2 ground risers on H-PAM-100 | +2 | Drawn DPs exceed markers; no 'connect to civil' note on PAM | 4 | M | ADOPT 4 per Rule 5 + RFI (connection point undefined - CL C8).
NBC vertical vent risers (Ø50/Ø75/Ø100, terminate 300mm above roof) | EA (riser) | - (17.06 m horizontal plan only) | ~13+ risers | NBC sheets/H-NBC-103: ~12 x Ø50, 1 x Ø75, 1 x Ø100 roof terminations | +13 (new) | Vertical heights not measurable in plan view - not in Denis's vent totals | 13 | L | ALLOWANCE - 13 risers; height per riser from sections/ceiling RLs at Phase 6; roof-colour flashings per SD8.
PAM vertical vent riser (Ø65 VP) | EA (riser) | - (1.93 m horizontal plan only) | 1 | H-PAM-100/101 (Ø65 VP to above roof) | +1 (new) | Vertical unmeasured (vent measure looks light per PAM note 6.4) | 1 | M | ALLOWANCE - single riser height from section at Phase 6.
Testing: 1-hour static water/drainage tests + certificates + third-party-signed photographic evidence | item | - (none in any legend) | n/a | H-NBC-002 / H-PAM-002 note G4; water test held until trench reinstatement complete | n/a | Obligation exists only as drawing note | ALLOWANCE (QA time + water + certification) | - | TPS both buildings + site sewer/sanitary; witness marks; as-con G16 separately in prelims.
CCTV of all in-ground drainage (independent approved firm, Superintendent present) | item | - (not counted) | n/a | VOL38 3.56; matrix 1.6 (both stages) | n/a | Never quantified | ALLOWANCE - each entity its own assets (TCS stormwater / TPS sewer) | - | Split per interface L15; no combined deliverable.
Hydrostatic pressure testing + disinfection of water/fire mains | item | - (not counted) | n/a | AS3500.1 / VOL38 testing regime | n/a | Never quantified | ALLOWANCE (TPS site + buildings) | - | Include booster/hydrant commissioning + FRQ 2-week notice (VOL38 12.17/25).
Articulation / expansion joints - reactive soil H1 'P' classification | EA / item | 2 counted (1 NBC + 1 PAM knuckle) | n/a | H-NBC-300 detail 1 (swivel/expanda/combo joints); AS/NZS 2032; AS3500.2 App G Class H1; DP expansion <=6 m spacing | n/a | H1 'P' requirement never counted beyond 2 joints | ALLOWANCE - Phase 6 count from drainage runs (joints at slab entries, risers, <=6 m DP spacing) | L | Increased provisions per CONFLICT_LOG G; lagging included.
Seismic bracing / restraints (AS1170.4 EDC 2, subsoil Ce) | item | - (not counted) | n/a | VOL38 3.15; H-NBC-301 HWU 25mm SS strap + Unistrut detail; H002 n.9 | n/a | Never quantified | ALLOWANCE - install + restraint LAYOUT drafting only (no engineering design liability per CL C7 / matrix X4) | - | Scissor/EWP access for ceiling-level restraint included in allowance.

## Opens
# | Source note(s) | Open item | Detail / why it matters | Proposed resolution | Owner
1 | groundplan_civil_sw 5.2 | 225 PVC DWV +65.5 m unexplained | Denis 180.93 m vs line-81 printed 115.45 m; source of the extra ~65 m unidentified (possibly building cut-off drains / bi-fold door outlets measured as 225, or a double run at the amenities building). Adopted 115.45 m - if real scope exists beyond line 81 it must be added back as a separate item. | Denis to identify what the extra polylines trace in the Groundplan native file | Denis
2 | groundplan_civil_sw 5.3 | RCP 375 CL4 extent (30.40 m vs ~12.0 m) | Long sections print CL4 only on line 05 (05-01 to 06-03, 11.988 m); which other runs make up Denis's 30.40 m CL4 unconfirmed. Adopted split CL3 702.9 / CL4 12.0 - class affects supply rate only. | Denis to identify runs classed CL4; correct split before Phase 6 rates | Denis
3 | civil_sw 4.4 vs vol15_long_sections | Independent RCP375 total discrepancy between our own notes | Take-off note cites design ~690.4 m; the long-section run-by-run sums give 714.9 m combined - line 06 start chainage -24.498 (24.5 m) appears dropped from the note's sum. Adopted the printed run sums (714.9 basis). This also corrects Rule 2's '~+35 m' overage to ~+10.6 m. | Re-run chainage sum at Phase 6 before rates locked | Phase 6
4 | civil_sw 5.5 / 5.6 | Identify Denis's specific missed structures | Which 1200 AC (of 25-03 / 26-02 / 26-03 / 26-05) and which P2P (60-02 or 81-04) are absent from his count. Totals adopted 4 / 20 regardless - only fitting-type pricing is affected. | Denis to confirm in Groundplan native file | Denis
5 | civil_sw 6.1 | Pipe material naming: 'HDPE PN100 SN8' vs drawings' PP | All 225-600 reticulation labelled PP on drawings is described as HDPE PN100 SN8 (PN100 is not a real class for this product). Lengths reconcile - same network. | Price as PP (StormPRO or equal); Denis confirm description intent | Denis
6 | civil_sw 6.3 / CL F1 | Kerb chutes - Director decision D6-F1 | 9 kerb chutes: Denis's 24-Jul email excludes entirely vs locked 5.3 rock+mat only. EA construction (concrete invert 1000x150, kerb returns, matting) unquantified either way. Adopted 9 EA count with disposition open. | Director decision D6-F1; both positions costed in EBC register | Director
7 | vol15 F1320 / CL D7 | GT2 'NO. PITS = 4' does not reconcile | GT2 141.2 m lists 4 pits vs GT3/GT4 (identical length/spacing) 7 each; layouts show 5 trash boxes + 7 connection structures along GT2. 'No. pits' column meaning undefined. | RFI - define pit count basis; adopted pit count from F1310 IDs meanwhile | RFI
8 | vol15 / CL D1/D6 | C09A/B end structures detailed nowhere | Twin 2x375 RCP culvert end structures appear in neither F1310 nor F1321; both ends labelled 'HEADWALL OUTLET'; C09B IL (34.911) above C09A (34.825) - flow direction unclear. | RFI - C09 headwall/apron/rock-pad details + flow direction | RFI
9 | vol15 / CL D2/D5 | F1310 pit schedule defects | 87-02 listed twice with conflicting attributes; remarks/cover columns shifted one row for ~5 pits (02-01, 81-07, 83-01, 87-01, 87-02); long section labels '81-08' vs schedule 81-07; reference typos (12306_12320, F650). | RFI - corrected pit schedule; priced on conservative reading meanwhile | RFI
10 | civil_sw 6.8 / CL E2/F2 | WSUD supply package re-quote | 22 OceanProtect StormFilter cartridges + DN3300 manhole internals: two stale Atlan figures ($106,221.80 email vs $88,838 workbook); Ocean Protect now nominated. | Re-quote Ocean Protect; PC Sum +15% supply+delivery, install inside TCS lump sum (L3) | Phase 6
11 | groundplan_sitework_hyd 6.2 | Ø20-to-25 / Ø25-to-32 upsizing convention | Runs labelled Ø20 taken off as 25 PE (74.25 m) and Ø25 as 32 PE (37.26 m); no Ø20 item exists. Kept per Rule 1. | Denis confirm deliberate estimating convention vs misread | Denis
12 | sitework 6.3 / matrix 2.1-c | Ø200 main material basis | Measured as Kembla copper Type B (134.63 m); locked 5.5 base offer is Ø200 ID HDPE PE100 SDR11 with no buried copper alternate. Length firm; rate basis must move to HDPE. | Phase 6 re-rate the 134.63 m run to HDPE PE100 SDR11 basis | Phase 6
13 | sitework 6.8 / CL C1/F3 | Fire service extent vs AS2419.1 | 217.73 m DN125 + 1 booster + 1 dual hydrant looks light; H003 prints no lengths and no legible hydrant symbols; H004 continuation missing from set. | RFI on design intent/coverage; Phase 4 AS2419.1 coverage check | RFI
14 | all five take-off notes | EA symbol counts not independently recounted | Dense symbol clusters (e.g. NBC 68x bend 100x90, 71x junction) accepted from Groundplan auto-legend; composite glyphs defeat automated counting. | Denis screen-zoom spot-check of the ten densest clusters in native files | Denis
15 | clubhouse 5.2/5.3 + vol06_11 | NBC drawn-vs-counted deltas adopted high | Hose tap 5th (NBC-201 symbol uncounted) and 20mm RPZD 4th (NBC-202 ~4 positions vs 3 counted) adopted; 'hot water pump' 1 counted vs vol06_11 'pumps: none shown'; possible 50mm/20mm RPZD position overlap. | Denis verify each against native file; adjust adopted counts if disproven | Denis
16 | pam 6.1/6.5/6.10 + 7 | PAM minor verifications | CO: 7 annotations vs 6 counted (adopted 7); TMV '(TYPICAL)' plural vs 1 counted; plan-F 0.45 m sewer pick-up no-double-count check; Cu20 0.96 m position unlocated. | Denis verify; TMV also allow-per-warm-water-group + RFI | Denis
17 | clubhouse 6.3 / pam 6.6 / CL C9 | 316 SS water spec vs copper measured | WS2 requires 316 SS press-fit >DN22 (and 316 SS external exposed connections); measured copper Type B: NBC 150.46 m + PAM 37.42 m combined. | Price stainless conforming + copper labelled alternate per locked 5.5; obtain SS press-fit rates | Phase 6
18 | fixture_count 5 / 7 | Fixture take-off incomplete - MATERIAL | Only Canteen/Kitchen + C/R.03/04 counted (25 EA); changerooms C/R.01/02, First Aid, Cleaners, Amenities M/F, PWD entirely uncounted (indicatively 15+ pans vs 1 counted). Interim adopted counts on Fixtures sheet are LOW confidence. | Denis rebuild counts for AR-NBC-3006/3007/3008/3009; reconcile line-by-line vs Tradelink 1066143 | Denis
19 | fixture_count 7 / CL F4 | Tradelink quote validity/escalation | $252,694.77 ex GST quote dated 15/07/26 expires 13/08/26 vs 2027 commencement; header address defect ('544 Yaamba Rd Parkhurst'). | Escalation + validity qualification in submission; re-quote near award | Phase 6
20 | fixture_count 6.2 | Architectural code list AR-NBC-0010 not held | Codes WC-04, Z.HB, H.EW, H.PB, N.WB, I.HM, H.TT-03/-04, HW-02/-04, H.TM-02 cannot be decoded; H.EW may be electric water heaters (would conflict with 2-HWU adoption). | RFI - obtain AR-NBC-0010 | RFI
21 | fixture_count 6.3 / CL C10 | ODF drinking fountain basis | Chilled (VOL25) vs non-chilled (VOL28) - same SKU DFCF400; 1 station vs 3 bowls pricing basis; elevations tag ODF on 3 faces vs 2 hydraulic fountains drawn. | RFI; carried as calculated PC Sum per matrix 4.12-e / 1B 4.5-c | RFI
22 | vol06_11 conflicts 7 | PAM 'TR' x2 undefined fixture label | North wall grid C, fed Ø20 DCW, drains via FWG - not in PAM-001 abbreviation list. Adopted 2 EA allowance. | RFI - fixture type + spec | RFI
23 | clubhouse 6.1 vs vol06_11 | NBC roof DP count unresolved | 19+ DPs per clubhouse-note reading of NBC-103 vs 11 roof callouts / 12 ground labels per vol06_11 dedicated review. 19 stubs adopted conservatively (NewItems #5). | RFI - confirm DP number/positions; correct stub count at Phase 4 | RFI
24 | vol06_11 conflicts 11 / CL B6 | Grease arrestor size | 1500L Viking PanelTim (H-NBC-102) vs 2000L (Design Report) vs Halgan 550-5000L no size selected (spec) - three sizes in three documents; no GIT install detail in volume. | RFI size selection; carried as PC/allowance | RFI
25 | clubhouse 6.4 | Trade-waste vent items on Vent layer | 1.98 m 110 HDPE + 2 bends recorded under Vent layer merged into TW package (54.78 m). Identical item names across layers merge automatically in roll-ups. | Phase 6 workbook check - count once, no layer-based double count | Phase 6
26 | vol15 F1305/F1323 / Rule 5 | Detention basin + spillway allocation | Basin earthworks and 50 m concrete spillway weir never quantified in any take-off set; allocation split between bulk earthworks trade and TCS drainage (1A 2.5) unconfirmed. Spillway 50 m adopted to TCS (NewItems #4); basin shaping left with earthworks per matrix 2.5-x4. | RFI + Director confirmation before close | Director
27 | sitework 5.1 / CL C4 | Sewer rising main discharge undefined | ~60-110 m Ø100 rising main unmeasured; discharge 'location to be confirmed and coordinated'; ownership ambiguous once Council installs the station. 110 m EBC allowance adopted (NewItems #1). | RFI - discharge point + scope ownership; keep EBC wording | RFI
28 | clubhouse 4 + vol06_11 could-not-verify | NBC TMV count basis | Denis counted 10 TMVs; vol06_11 found no TMV count or cabinet note on NBC-200/201/202 (PAM has the 1600 AFFL note). Adopted 10. | Denis confirm locations; allow per warm-water fixture groups + RFI | Denis