## TCS_Activities
ID | Stage | Work area | System | Activity | Adopted qty | Unit | Prod rate | Rate basis (stated) | Labour conf (H/M/L) | Crew | Crew size | Duration (10-hr days) | Crew-days | Ordinary hrs (crew) | Supervision hrs (LH alloc) | Plant items + days | Consum./small tools | Status | Notes
A-01 | 1A | Sitewide | Prelims | Site establishment - TCS own compound, temp services (no shared prelims) | 1 | item | 3 days | Estimator judgement - standalone establishment incl own toilets/wash/genset/potable water storage (ITT S17.3: no site power or water); access Norman Rd only | M | Civil Crew A | 3 | 3 | 3 | 90 | 15.5 | 6T tipper 3d; genset (hire) | Y | Base | Each entity carries full load per SS5.2; rumble grid/washdown compliance (VFMP)
A-02 | 1A | Sitewide | Prelims | Set-out survey + DBYD / service location | 1 | item | 2 days | Estimator judgement - trade set-out from Principal-supplied control (matrix 1.5); locator for live irrigation lines under ex-fields (geotech S2.0) | M | Civil Crew A | 3 | 3 | 3 | 90 | 15.5 | Services locator subbie 1d @$130/hr | N | Base | Surveyor subbie $180/hr as-needed
A-03 | 1A | Fields / roads | Stormwater mainline | RCP375 CL3 mainline incl C09 twin barrels | 702.9 | m | 45 m/day | Estimator judgement - typical CQ civil crew 55-60 m/day, 375 RCP in stiff clay at 0.8-1.3 m invert (vol15); LESS 15-20% flat-grade laser penalty (runs at 1:500 / 1:250, 1:248 grades - tight level control obligation vol15 Obl.1) | M | Civil Crew A | 3 | 16 | 16 | 480 | 82.4 | 13-16T excavator 16d; trench roller 16d; 6T tipper 16d | Y | Base | Depths all <1.5 m - batter/bench not triggered; open-trench minimised per geotech S5.3.3
A-04 | 1A | Fields | Stormwater mainline | RCP375 CL4 + RCP600 CL3 short runs | 15.3 | m | 15 m/day | Estimator judgement - short isolated runs; RCP600 at 1 in 500 (0.20%) grade = laser run penalty (vol15) | M | Civil Crew A | 3 | 1 | 1 | 30 | 5.2 | 13-16T excavator 1d | N | Base | CL4->CL3 re-split per adopted qty (Opens #2)
A-05 | 1A | Netball courts | Stormwater collectors | PP collector mains 225/300/375/450/600 - 17 m court bays | 486.6 | m | 50 m/day | Estimator judgement - lighter PP pipe handles faster than RCP; offset by pipe-to-pipe junction each 17 m bay + flat grades (0.66-0.71%) | M | Civil Crew A | 3 | 10 | 10 | 300 | 51.5 | 13-16T excavator 10d; trench roller 10d; 6T tipper 10d | Y | Base | Court-area congestion with courts subgrade contractor - sequence before pavement
A-06 | 1A | Fields | Building drainage collector | 225 PVC DWV line 81 (adopted 115.45 m per long-sections) | 115.45 | m | 60 m/day | Estimator judgement - shallow (0.33-0.97 m) PVC in clay | M | Civil Crew A | 3 | 2 | 2 | 60 | 10.3 | 5T excavator 2d | N | Base | Line 81/83/87 all-TCS per corrected POD boundary (matrix 2.5-x5)
A-07 | 1A | Sitewide | Laterals | 100 PVC DWV subsoil outlets / building DP laterals | 283.71 | m | 80 m/day | Estimator judgement - small-bore shallow PVC; fittings-heavy (17x90, 9x45 bends, 26 junctions) | M | Civil Crew A | 3 | 4 | 4 | 120 | 20.6 | 5T excavator 4d; wacker 4d | N | Base | Subsoil SYSTEM itself excluded (by others) - outlets/connections at TCS pits only (L12)
A-08 | 1A | Sitewide | Rock | Rock extra-over trenching allowance (rock-affected band) | allowance | item | 10 crew-days | Geotech NQL2024-0320: refusal 25/36 locations; XW rock 0.2-2.2 m at 6 pits (TP03 0.70 m, TP/CBR05 0.9 m, TP/CBR07 1.1 m); with typical inverts 0.8-1.3 m, ~15% of trench metres assumed rock-affected at ~40% production | L | Civil Crew A | 3 | 10 | 10 | 300 | 51.5 | Breaker 13-15T 10d @$203/d; 20-24T excavator 10d | N | Base (allowance) | ITT S18.2 pays rock ONLY on written direction + survey - allowance covers programme/production risk, rates tendered separately (7.0-a)
A-09 | 1A | Sitewide | QA | Testing + CCTV attendance - TCS drainage assets (VOL38 S3.56) | 1 | item | 4 days | Estimator judgement - crew attendance on independent CCTV firm + static tests; water cartage required (no site water, ITT S17.3) | M | Civil Crew A | 3 | 4 | 4 | 120 | 20.6 | Water truck 2d @$110/hr; CCTV subbie (PC) | N | Base | Superintendent present for CCTV; 1-hr static tests + certificates
A-10 | 1A | Sitewide | QA | As-constructed survey + ADAC XML attendance (own assets) | 1 | item | 3 days | Estimator judgement - pickup attendance; surveyor subbie $180/hr; RPEQ cert by others engaged by TCS | M | Civil Crew A | 3 | 3 | 3 | 90 | 15.5 | Surveyor subbie 3d | N | Base | ADAC XML mandatory for Council assets (ITT S19)
A-11 | 1A | Sitewide | Risk | EDQ-gate remobilisation allowance (Conditions 16/17 - 20-business-day reviews gate stormwater start) | 1 | item | 4 crew-days | RPT006_B S3.1 - stormwater drawings + WSUD memo resubmissions outstanding, on critical path; carried as one remobilisation line, NOT spread across rates | L | Civil Crew A | 3 | 4 | 4 | 120 | 20.6 | Plant float 2 loads @$200/hr | N | Base (allowance) | If gate clears pre-possession this line returns as saving
A-12 | 1B | 1B area | Prelims | Stage 1B establishment / remobilisation (standalone per SS5.2) | 1 | item | 2 days | Estimator judgement - 1B must stand alone if awarded alone | M | Civil Crew A | 3 | 2 | 2 | 60 | 10.3 | Tipper 1d | N | Base | Priced in 1B roll-up only
A-13 | 1B | 1B area | QA | 1B testing / CCTV / ADAC share | 1 | item | 2 days | Estimator judgement | M | Civil Crew A | 3 | 2 | 2 | 60 | 10.3 | Water truck 1d | N | Base
B-01 | 1A | Roads / carpark | Pits | RGU inlets on-grade 28 + sag 5 (CMDG-D-020, 2.4 m lintels) | 33 | EA | 1.5 EA/day | Estimator judgement - precast RGU + lintel, bench, connect, backfill; all shallow (<1.3 m) | M | Civil Crew B | 3 | 22 | 22 | 660 | 113.3 | 8T excavator 22d; wacker 22d; franna/HIAB deliveries | Y | Base
B-02 | 1A | Sitewide | Pits | 1050 access chambers (CMDG-D-030) | 13 | EA | 1.0 EA/day | Estimator judgement - typical CQ precast chamber cycle at <1.3 m | M | Civil Crew B | 3 | 13 | 13 | 390 | 67 | 8T excavator 13d; wacker 13d | Y | Base
B-03 | 1A | Sitewide | Pits | 1200 access chambers incl 26-02 internal upstand (0.467 m) | 4 | EA | 0.75 EA/day | Estimator judgement + formwork for deliberate IL upstand at 26-02 (vol15 conflict 5 - verify F1320 detail) | M | Civil Crew B | 3 | 6 | 6 | 180 | 30.9 | 8T excavator 6d | Y | Base
B-04 | 1A | Fields | Pits | 600x600 field inlets Type 2 (CMDG-D-022) | 3 | EA | 2 EA/day | Estimator judgement | H | Civil Crew B | 3 | 2 | 2 | 60 | 10.3 | 8T excavator 2d | N | Base
B-05 | 1A | Sitewide | Structures | Pipe-to-pipe connections (junctions without access structures) | 20 | EA | 3 EA/day | Estimator judgement - cut-in junctions; workmanship obligation vol15 Obl.5 | M | Civil Crew B | 3 | 7 | 7 | 210 | 36.1 | 8T excavator 7d | N | Base
B-06 | 1A | Outfalls | Structures | Pipe headwalls (375 x5, 2x375 x2, 225 x1, 300 x1, 150 x1) | 10 | EA | 1.0 EA/day | Estimator judgement - precast/cast headwall + apron at swale outfalls; DTMR/CMDG | M | Civil Crew B | 3 | 10 | 10 | 300 | 51.5 | 8T excavator 10d | Y | Base | C09A/B both labelled OUTLET - RFI (vol15 conflict 3)
B-07 | 1A | Detention basin | Structures | Concrete spillway weir (F1323 build-up) | 50 | m | 5 m/day | Estimator judgement - formed/poured concrete weir incl subgrade trim; allocation RFI + Director (Opens #26); basin embankment design not final (RPT006_B S5.1.3) | L | Civil Crew B | 3 | 10 | 10 | 300 | 51.5 | 5T excavator 5d; concrete gear; concreter subbie option $145-185/m | Y | Base | Scope-change risk flagged - basin footprint increased at 100%DD
B-08 | 1A | Outfalls | Erosion protection | Rock pads / beaching at headwalls + basin (excl kerb-chute rock) | 513.3 | m2 | 60 m2/day | Estimator judgement - D50 100-500 rock placement by excavator + hand trim | M | Civil Crew B | 3 | 9 | 9 | 270 | 46.4 | 5T excavator 9d; 6T tipper 9d | N | Base | Basin rock D50=500 depth 900 at C10 = machine placement
B-09 | 1A | Roads | Structures | Kerb chutes 9 no. (concrete invert + kerb returns + rock/mat) | 9 | EA | 1.0 EA/day | Estimator judgement - EBC BOTH POSITIONS per Director decision D6-F1 (full exclusion vs rock+mat only) | L | Civil Crew B | 3 | 9 | 9 | 270 | 0 | 5T excavator 9d | Y | EBC - excluded from base totals | D6-F1 pending; 55.67 m2 rock+mat sits in B-08 scope if reinstated
C-01 | 1A | Detention basin | Culverts | C10 RCBC 2700x1200 basin outlet - heavy lift, cover 0.11-0.15 m | 17.53 | m | 3 m/day | Estimator judgement - ~8-10 t units, 50t crane set; embankment built over by others (sequencing interface); invert 1.31-1.35 m + base = shields for entered excavation per geotech (<2 m batters 1.5H:1V else shields) | M | Civil Crew C | 3 | 6 | 6 | 180 | 30.9 | 20-24T excavator 6d; 50t crane ALLOWANCE 6d (not in hire register); 6T tipper 6d; shields 6d | Y | Base | First activity - drainage outfall established early
C-02 | 1A | Paths / swales | Culverts | RCBC small culverts 600x300 (C05-C08), 750x300, 900x450 (C01/C02) | 66.42 | m | 8 m/day | Estimator judgement - light units BUT zero/negative cover at headwalls (vol15) = surface tie-in + trim penalty; confirm load class vs traffic | M | Civil Crew C | 3 | 9 | 9 | 270 | 46.4 | 20-24T excavator 9d; franna ALLOWANCE 9d; tipper 9d | Y | Base | 750x300 = WSUD high-flow bypass at tank cluster
C-03 | 1A | Access road | Culverts | RCBC 1200x600 (C03) + 1500x600 (C04) | 46.81 | m | 6 m/day | Estimator judgement - mid-size boxes, C04 cover only ~0.17-0.37 m; access-road cross drainage designed to 2% AEP | M | Civil Crew C | 3 | 8 | 8 | 240 | 41.2 | 20-24T excavator 8d; franna ALLOWANCE 8d; tipper 8d | Y | Base
C-04 | 1A | Outfalls | Culvert structures | Culvert headwalls C01-C10 A/B incl wingwalls + rock beaching interface | 20 | EA | 1.25 EA/day | Estimator judgement - DTMR/CMDG headwall/wingwall units, several proud of surface (negative cover) needing landscape tie-in | M | Civil Crew C | 3 | 16 | 16 | 480 | 82.4 | 20-24T excavator 16d | Y | Base | C09A/B details missing - RFI carried
C-05 | 1A | SW corner courts | WSUD | WSUD DN3300 manhole install + 22 StormFilter cartridges (supply = PC Sum +15%) | 1 | EA | 8 days | Estimator judgement - deepest excavation in TCS scope (invert 1.57-1.67 m + founding, exceeds 1.5 m bench = geotech entry inspection per NQL2024-0320 S5.3.3); shields; wet-season seepage pumping from sumps; crane set of DN3300 sections + internals | L | Civil Crew C | 3 | 8 | 8 | 240 | 41.2 | 20-24T excavator 8d; 50t crane ALLOWANCE 2d; shields 8d; sump pumps 8d; dewatering | Y | Base | Ocean Protect re-quote at Phase 6 (Opens #10); EDQ Cond 16 gates start
C-06 | 1A | Netball courts | Trench drains | Grated trench drains GT1-GT4 + GT7-GT9 (Hauraton Recyfix, court edges) | 561.9 | m | 25 m/day | Estimator judgement - proprietary channel on concrete bed + haunch at court edge; laser precision against court FSL; follows courts pavement by others (assumed available day 85) | L | Civil Crew C | 3 | 23 | 23 | 690 | 118.5 | 5T excavator 23d; concrete gear; quick-cut 5d | Y | Base | Sch 1A 3.5 TCS despite Hydraulic heading (locked); GT2 4-pits RFI
C-07 | 1A | Netball courts | Trench drains | Trash Box 200 x25 + 150 DWV laterals lines 30-53 (grades to 29.2%) | 25 | EA | 2 EA/day | Estimator judgement - box set + short steep lateral (1.0-1.6 m) + connect to trunk pit each | M | Civil Crew C | 3 | 13 | 13 | 390 | 67 | 5T excavator 13d; wacker 13d | Y | Base
C-08 | 1B | Multi-use court / PAM | Trench drains | GT5 (Recyfix 100) + GT6 (Recyfix 200 D400 ductile) trench drains | 46.6 | m | 20 m/day | Estimator judgement - short runs, D400 ductile handling at PAM (Class D outlier noted) | M | Civil Crew C | 3 | 3 | 3 | 90 | 15.5 | 5T excavator 3d | Y | Base | 1B roll-up; stage split per VOL 20 hatch (RFI)
C-09 | 1B | District park | Drainage | Lines 60/61/83 150 PVC DWV (~29.6 m) + Trash Box 100 x4 + field inlet share | 1 | lot | 4 days | Estimator judgement - small scattered runs, depths 0.37-0.92 m | M | Civil Crew C | 3 | 4 | 4 | 120 | 20.6 | 5T excavator 4d | N | Base | 1B roll-up
ROLL-UP |  |  |  | TCS (Civil Stormwater) BASE total | [7 empty] | 233 | 233 | 6990 | 1200 |  |  |  | Stage 1A 222 cd / Stage 1B 11 cd; crews of 3 (2 Trades + 1 TA); LH supervision 120 days x 10 hr
ROLL-UP |  |  |  | TCS (Civil Stormwater) EBC (excluded from base) | [7 empty] | 9 | 9 | 270 | 0 |  |  |  | B-09 Kerb chutes 9 no. (concrete invert + ker
INDICATIVE LABOUR $ (clearly marked - indicative @ uplifted rates: LH $132.9634/hr, Trades $101.6458/hr, TA $82.9510/hr, ex GST)
|  |  |  | Crew labour (base) | [14 empty] | 233 cd x $2,862.43 = $666,945
|  |  |  | Supervision (LH) | [14 empty] | 120 d x $1,329.63 = $159,556
|  |  |  | TOTAL indicative labour | [14 empty] | $826,501 ex GST - INDICATIVE ONLY, pricing at Phase 6
PLANT ROLL-UP (dry hire unless noted; day rates ex GST from Equip_HIRE registers - header says WEEKLY (5 day) but unit column says Day: treated as $/day, FLAGGED for Phase 6 confirmation)
Item | Total days | Indicative rate/day | Source | Flag
13-16T excavator | 43 | $317.20 | Hyd Equip_HIRE_Master | Mainline/PP/DWV trenching
8T excavator | 64 | $261.17 | Hyd Equip_HIRE_Master | Crew B pits/structures
20-24T excavator | 66 | $314.29 | Hyd Equip_HIRE_Master | Culverts, WSUD, rock band
3-5T excavator | 68 | $238.67 | Hyd Equip_HIRE_Master | GT, trash boxes, laterals, rock pads
Breaker 13-15T | 10 | $203.00 | Hyd Equip_HIRE_Master | Rock extra-over band only
Trench roller dbl drum | 60 | $165.00 | Hyd Equip_HIRE_Master | Shared A/B
Upright rammer/wacker | 70 | $34.29 | Hyd Equip_HIRE_Master
<6T tipper | 70 | $171.43 | Hyd Equip_HIRE_Master
50t mobile crane | 8 | ALLOWANCE ~$3,800/d wet | NOT in hire registers | C10 + WSUD sets - quote at Phase 6
Franna/pick-and-carry | 17 | ALLOWANCE ~$2,200/d wet | NOT in hire registers | Culvert units - quote at Phase 6
Trench shields | 14 | ALLOWANCE ~$120/d | NOT in hire registers | WSUD + C10 + entered runs per geotech
Vacuum excavator (TPZ/services) | 6 | $295.77 | Hyd Equip_HIRE_Master | VFMP water-excavation in NRZs (arborist-supervised)
Water truck (test/flush cartage) | 3 | $110/hr wet | Misc Subbie Rates | No site water - ITT S17.3
Sump pumps/dewatering | 10 | $57/d (flexdrive set) | Hyd Equip_HIRE_Master | Wet-season seepage per geotech S4.2

## TPS_Activities
ID | Stage | Work area | System | Activity | Adopted qty | Unit | Prod rate | Rate basis (stated) | Labour conf (H/M/L) | Crew | Crew size | Duration (10-hr days) | Crew-days | Ordinary hrs (crew) | Supervision hrs (LH alloc) | Plant items + days | Consum./small tools | Status | Notes
T1-01 | 1A | Sitewide | Prelims | Site establishment - TPS own compound + temp services (no shared prelims) | 1 | item | 3 days | Estimator judgement - standalone per SS5.2; own toilets/wash/genset/potable water storage + distribution (ITT S17.3 no site power/water) | M | Crew 1 In-Ground Drainage | 3 | 3 | 3 | 90 | 25.3 | Tipper 2d; genset (hire); potable water pods | Y | Base | Access Norman Rd only; VFMP washdown
T1-02 | 1A | Sitewide | Prelims | Set-out + DBYD / service location (live Ø300 main + irrigation under ex-fields) | 1 | item | 2 days | Estimator judgement - locator + potholing near live authority main | M | Crew 1 In-Ground Drainage | 3 | 2 | 2 | 60 | 16.9 | Services locator 1d @$130/hr; vac trailer 1d | N | Base
T1-03 | 1A | Site mains | Sewer gravity | Gravity sewer DWV PVC 150 (29.29 m) + 100 (178.24 m) @ 1:60 | 207.53 | m | 40 m/day | Estimator judgement - small-bore gravity at grade control 1:60; depths increase toward pumpwell ('adequate depth for gravity' RPT006 S12.1.1) - deeper legs assumed to 1.8 m = shields for entered runs per geotech | M | Crew 1 In-Ground Drainage | 3 | 6 | 6 | 180 | 50.6 | 5T excavator 6d; trench roller 6d; tipper 6d; shields 2d | Y | Base | Terminates at Council pump station inlet DICL piece (L6)
T1-04 | 1A | Site mains | Sewer structures | SMS x2 + Ø150 property connection into existing MH (location TBC) | 3 | EA | 1 EA/day | Estimator judgement - maintenance shafts + live-MH connection under FRW attendance; hydro-excavation around existing services | M | Crew 1 In-Ground Drainage | 3 | 3 | 3 | 90 | 25.3 | 5T excavator 3d; hydro-ex truck 1d @$190/hr | N | Base | FRW Private Works lodgement = Principal Contractor (X2)
T1-05 | 1A | Site mains | Trade waste / storm stubs | Site 110 HDPE trade waste run (16.28 m) + DWV 225 storm connection stubs (10 no.) | 1 | lot | 2 days | Estimator judgement - short runs + 10 stubs 0.49-0.98 m to civil connection points | M | Crew 1 In-Ground Drainage | 3 | 2 | 2 | 60 | 16.9 | 5T excavator 2d; electrofusion kit | N | Base | Storm stubs end at CONNECT TO CIVIL (TCS beyond - L2)
T1-06 | 1A | Site mains | Sewer rising main | Ø100/DN110 rising main pumpwell->discharge (EBC - 110 m allowance) | 110 | m | 55 m/day | Estimator judgement - small-bore PE in common trench conditions; EXCLUDED-BUT-COSTED pending discharge-point RFI (CL C4) + Council station boundary | L | Crew 1 In-Ground Drainage | 3 | 2 | 2 | 60 | 0 | 5T excavator 2d; butt welder 1d | N | EBC - excluded from base totals | Add-price ready for reinstatement
T1-07 | 1A | NBC | UG drainage rough-in | NBC under-slab sanitary DWV 100/50/40 (268.4 m) + fittings-heavy set (75+66 bends, 80 junctions) | 268.36 | m | 20 m/day | Estimator judgement - under-slab work between bored piers / suspended ground beams on H1 'P' reactive site; articulation joints at every beam penetration; congestion penalty ~30% vs open trench | M | Crew 1 In-Ground Drainage | 3 | 14 | 14 | 420 | 118.1 | 1.8T excavator 10d; 3-5T combo 4d; wacker 10d | Y | Base | Builder pier/beam completion gates start (assumed day 64)
T1-08 | 1A | NBC | UG trade waste | NBC trade waste 110 HDPE (54.78 m) + Geberit 50 + 1500L Viking GIT install | 1 | lot | 8 days | Estimator judgement - HDPE electrofusion/butt-weld system + GIT excavation/set (size conflict 1500/2000/550-5000L -> allowance basis, CL B6) | M | Crew 1 In-Ground Drainage | 3 | 8 | 8 | 240 | 67.5 | 3-5T excavator 4d; electrofusion + butt welder 6d; crane truck 1d | Y | Base | GIT final size TBC pending kitchen layouts
T1-09 | 1B | PAM | UG drainage rough-in | PAM under-slab sanitary DWV 100/50 (68.1 m) + ORG + FWG x4 | 68.09 | m | 20 m/day | Estimator judgement - same pier/ground-beam congestion basis as NBC | M | Crew 1 In-Ground Drainage | 3 | 4 | 4 | 120 | 33.7 | 1.8T excavator 4d; wacker 4d | Y | Base | 1B roll-up; PAM structure availability assumed day 148
T1-10 | 1A | NBC+PAM | DP stubs | Roof-DP in-ground connection stubs to CONNECT TO CIVIL (NBC 19 + PAM 4) | 23 | EA | 6 EA/day | Estimator judgement - short stubs at building perimeter; count L-confidence (11 vs 12 vs 19 unresolved - Opens #23) | L | Crew 1 In-Ground Drainage | 3 | 4 | 4 | 120 | 33.7 | 1.8T excavator 4d | N | Base | PAM connection point undefined - RFI (CL C8)
T1-11 | 1A | Sitewide | QA | CCTV + testing attendance - TPS sewer/drainage assets | 1 | item | 3 days | Estimator judgement - attendance on independent CCTV + 1-hr static tests; temp water cartage (no site water) | M | Crew 1 In-Ground Drainage | 3 | 3 | 3 | 90 | 25.3 | Water truck 1d @$110/hr; CCTV subbie (PC) | N | Base
T1-12 | 1A | Sitewide | Risk | Builder-window / EDQ remobilisation allowance | 1 | item | 4 crew-days | Estimator judgement - TPS building works follow builder structure; 3 separate mobilisations assumed (site mains / rough-in / fit-off); carried as line, not spread | L | Crew 1 In-Ground Drainage | 3 | 4 | 4 | 120 | 33.7 | Plant float 2 loads | N | Base (allowance)
T2-01 | 1A | Site mains | Water main | Ø200 site main - base offer HDPE PE100 SDR11 (tapping to meter slab) | 134.63 | m | 30 m/day | Estimator judgement - large-bore PE incl butt-welded strings, lower/lay/backfill; 600 mm cover | M | Crew 2 In-Ground Water/Fire | 3 | 5 | 5 | 150 | 42.2 | 13-16T excavator 5d; PE BUTT WELDER ALLOWANCE 5d (not in hire register, allow ~$350/d); trench roller 5d; tipper 5d | Y | Base | Base = HDPE per SS5.5; copper alternate priced separately (matrix 2.1-c)
T2-02 | 1A | Site mains | Water connection | Authority Ø300 tapping cluster + valves/stubs (6 gasket kits, 3 SVs, tee/bends) | 1 | lot | 3 days | Estimator judgement - live-main connection under FRW attendance; hydro-excavation exposure; shutdown window risk | M | Crew 2 In-Ground Water/Fire | 3 | 3 | 3 | 90 | 25.3 | Hydro-ex truck 1d @$190/hr; 8T excavator 3d | Y | Base | FRW completes/coordinates connection as written (ITT S16) - physical works TPS
T2-03 | 1A | Site mains | Metering | 100 fire + 100 CW meter assemblies + 4x2 m slab + bollards | 1 | lot | 4 days | Estimator judgement + CONGESTION PENALTY at meter slab cluster (meters, RPZDs, booster cabinet, bin store, entry-sign services corridor per RPT006 S9.1) | M | Crew 2 In-Ground Water/Fire | 3 | 4 | 4 | 120 | 33.7 | 8T excavator 2d; concrete gear | Y | Base | Slab may move to concreter by builder direction (L7) - priced once here
T2-04 | 1A | Site mains | CW spine | 125 PE100 CW spine (8 runs) | 236.88 | m | 45 m/day | Estimator judgement - mid-bore PE, EF fittings | M | Crew 2 In-Ground Water/Fire | 3 | 6 | 6 | 180 | 50.6 | 13-16T excavator 6d; butt welder/EF 6d; roller 6d | Y | Base
T2-05 | 1A | Site mains | CW take-offs | Take-off sets: 6x100 SV/check/gaskets, 12 MaxiStubs, EF tees/reducers, caps | 1 | lot | 3 days | Estimator judgement - fitting-intensive cluster work | M | Crew 2 In-Ground Water/Fire | 3 | 3 | 3 | 90 | 25.3 | EF processor 3d | N | Base | Capped future services incl HPC/NBC/maintenance take-offs
T2-06 | 1A | Site mains | CW small-bore | 32/25 PE branch runs (111.5 m) + hose tap + caps | 111.51 | m | 60 m/day | Estimator judgement - small-bore PE | H | Crew 2 In-Ground Water/Fire | 3 | 2 | 2 | 60 | 16.9 | 1.8T excavator 2d | N | Base
T2-07 | 1A | Site mains | Fire main | 125 HDPE SDR11 REDLINE fire main (3 runs) | 217.73 | m | 45 m/day | Estimator judgement - as CW spine; AS2419.1 coverage check pending (extent qualified, CL F3) | M | Crew 2 In-Ground Water/Fire | 3 | 5 | 5 | 150 | 42.2 | 13-16T excavator 5d; butt welder 5d; roller 5d | Y | Base
T2-08 | 1A | Site mains | Fire appurtenances | 150 H-pattern booster assembly + cabinet + 100 dual pillar hydrant | 1 | lot | 3 days | Estimator judgement - booster set/plumb/cabinet + hydrant riser | M | Crew 2 In-Ground Water/Fire | 3 | 3 | 3 | 90 | 25.3 | 8T excavator 1d; crane truck 1d | Y | Base | Booster long-lead flagged
T2-09 | 1B | 1B services | Water/sewer branches | 1B branch take-offs: PAM Ø25/Ø32 entries, Ø100 PAM sewer leg, bubbler/DF supplies + wastes, hose taps | 1 | lot | 4 days | Estimator judgement - scattered small-bore branches from through-mains (branch fitting = 1A/1B line, L9) | M | Crew 2 In-Ground Water/Fire | 3 | 4 | 4 | 120 | 33.7 | 1.8T excavator 4d | N | Base | 1B roll-up
T2-10 | 1A | Site mains | Testing | Hydrostatic pressure test + disinfection - water/fire mains (temp water carted) | 1 | item | 4 days | Estimator judgement + FULL hydro test subbie $1,945/test x3 systems (Misc Subbie Rates); boost test $3,560; NO SITE WATER (ITT S17.3) - potable cartage + storage for test/flush water | M | Crew 2 In-Ground Water/Fire | 3 | 4 | 4 | 120 | 33.7 | Water truck 2d @$110/hr; test pump (subbie incl); potable storage pods | Y | Base | Form 72 $350 (subbie rate)
T3-01 | 1A | NBC | AG drainage | NBC stacks + vent risers x13 (Ø50/75/100, terminate 300 mm above roof) + horiz vent | 13 | riser | 2.2 riser/day | Estimator judgement - riser count is an ALLOWANCE (plan shows horizontals only - NewItems #7); roof penetrations coordinated with roofer | L | Crew 3 Above-Ground Drainage | 3 | 6 | 6 | 180 | 50.6 | Scissor lift 4d; podium/ladders | Y | Base | Mech-vs-arch ventilation conflict may add penetrations (RPT006 conflict 1)
T3-02 | 1A | NBC | AG waste | NBC above-ground waste 50/40 + tundishes (in-wall x4 + 4), FW connections, basket traps | 1 | lot | 5 days | Estimator judgement - wet-area count driven; fixtures-count risk flows here too | M | Crew 3 Above-Ground Drainage | 3 | 5 | 5 | 150 | 42.2 | Podium/ladders | Y | Base
T3-03 | 1B | PAM | AG drainage | PAM Ø65 vent riser + AG waste connections | 1 | lot | 2 days | Estimator judgement | M | Crew 3 Above-Ground Drainage | 3 | 2 | 2 | 60 | 16.9 | Ladders | N | Base | 1B roll-up
T3-04 | 1A | NBC | Seismic | Seismic restraint - drainage (AS1170.4 EDC2, subsoil Ce) - install + layout drafting only | 1 | item | 3 days | Estimator judgement - restraint at hangers/risers; NO engineering design liability (CL C7/X4); EWP access | L | Crew 3 Above-Ground Drainage | 3 | 3 | 3 | 90 | 25.3 | Scissor lift 3d | Y | Base | Adder kept as separate line per brief
T4-01 | 1A | NBC | Water rough-in | NBC water rough-in: PEX 223 m + copper/316SS 150 m + PE 64.5 m + B-press fitting set | 437.6 | m | 38 m/day | Estimator judgement - blend: PEX 60 m/day, hard-drawn 25 m/day, PE 45 m/day; in-wall/ceiling rough-in with blockwork coordination; CONFORMING 316 SS press-fit >DN22 slower than copper (+25% on hard-drawn share) - both-ways pricing per SS5.5 | M | Crew 4 Above-Ground Water/Fire | 3 | 12 | 12 | 360 | 101.2 | Press tool + jaws; scissor lift 4d | Y | Base | 316SS material long-lead flagged
T4-02 | 1A | NBC | Valving | NBC TMVs x10 + RPZD/check sets + isolation valves | 1 | lot | 3 days | Estimator judgement - TMV in lockable cabinets + commissioning-ready set | M | Crew 4 Above-Ground Water/Fire | 3 | 3 | 3 | 90 | 25.3 | Podium | N | Base
T4-03 | 1A | NBC | Hot water | 2x Rheem 315L HWU + HW circulating pump + flow/return loop | 1 | lot | 3 days | Estimator judgement - adopted 2 HWU (double-count removed); pump conf L (Opens #15) | M | Crew 4 Above-Ground Water/Fire | 3 | 3 | 3 | 90 | 25.3 | Crane truck 0.5d | Y | Base
T4-04 | 1A | NBC | Fire | NBC FHR x1 + FB x1 (FE x8 = EBC, supply ownership RFI CL B8) | 1 | lot | 1 day | Estimator judgement | M | Crew 4 Above-Ground Water/Fire | 3 | 1 | 1 | 30 | 8.4 | - | N | Base | AS1851 12-month maintenance priced in commercial build
T4-05 | 1B | PAM | Water rough-in | PAM water rough-in: copper/316SS 37.4 m + PEX 24.8 m + PE 3.3 m + in-wall cistern feeds | 65.5 | m | 20 m/day | Estimator judgement - small building, blockwork in-wall cisterns x8 slow the runs | M | Crew 4 Above-Ground Water/Fire | 3 | 4 | 4 | 120 | 33.7 | Press tool | Y | Base | 1B roll-up
T4-06 | 1B | PAM | Hot water | PAM Rheem 50L HWU + TMV + Ø32 check-meter assembly | 1 | lot | 1 day | Estimator judgement - no PRV shown vs NBC 500 kPa - RFI | M | Crew 4 Above-Ground Water/Fire | 3 | 1 | 1 | 30 | 8.4 | - | N | Base | 1B roll-up
T4-07 | 1A | NBC | Seismic | Seismic restraint - water services (EWP) - install + layout drafting only | 1 | item | 2 days | Estimator judgement - as T3-04 basis | L | Crew 4 Above-Ground Water/Fire | 3 | 2 | 2 | 60 | 16.9 | Scissor lift 2d | Y | Base
T5-01 | 1A | NBC | Fit-off | NBC fixture fit-off (~93 fixtures: 21 WC, 14 basins, 10 showers, 3 urinals, 9 troughs, CSK, 22 FW, kitchen sinks, PWD suite) | 93 | EA | 7 EA/day | Estimator judgement - 2.3 fixtures/day/man for quality commercial suites incl AS1428 sets; FIXTURE COUNTS ARE L-CONFIDENCE (Phase 4 recount AR-NBC-3006-3009 + Tradelink reconciliation mandatory) | L | Crew 5 Fit-Off / Misc | 3 | 13 | 13 | 390 | 109.6 | Podium; small tools | Y | Base | Largest single TPS labour risk with count risk attached
T5-02 | 1A | NBC | Fit-off specialties | Kitchen/canteen: Billi install (RCC-supplied) + Stoddart sink benches taphole/connect + spray rinse + GIT commissioning | 1 | lot | 3 days | Estimator judgement - benchwork coordination, tapholes drilled onsite (VOL 25) | M | Crew 5 Fit-Off / Misc | 3 | 3 | 3 | 90 | 25.3 | Small tools | Y | Base
T5-03 | 1B | PAM | Fit-off | PAM fit-off: 8x s/s WC + in-wall cisterns, 1800 trough, PWD basin, CSK, 2 TR, timed taps | 1 | lot | 4 days | Estimator judgement - in-wall cistern commissioning + s/s fixture sets; TR label undefined (RFI) | M | Crew 5 Fit-Off / Misc | 3 | 4 | 4 | 120 | 33.7 | Small tools | Y | Base | 1B roll-up
T5-04a | 1A | NBC external | Fit-off | ODF drinking fountains x2 (chilled - PC Sum) incl water/waste connections | 2 | EA | 2 EA/day | Estimator judgement - external units in paving zone by others | M | Crew 5 Fit-Off / Misc | 3 | 1 | 1 | 30 | 8.4 | Small tools | N | Base | Chilled/non-chilled SKU RFI (CL C10)
T5-04b | 1B | Rec park | Fit-off | Water bubbler stations install (PC Sum units) + supply/waste connections | 1 | lot | 1 day | Estimator judgement - units undefined in legend (RFI CL C10); connections priced 1B 2.2-b | L | Crew 5 Fit-Off / Misc | 3 | 1 | 1 | 30 | 8.4 | Small tools | N | Base | 1B roll-up
T5-05 | 1A | NBC | Articulation | Articulation adder - H1 'P' reactive site: expansion/knuckle joints at slab entries, risers, <=6 m DP spacing | 1 | item | 3 days | Allowance per NewItems #12 - joint count to be fixed Phase 6 from drainage runs; geotech H1 'P' + bored-pier/ground-beam structure drives count | L | Crew 5 Fit-Off / Misc | 3 | 3 | 3 | 90 | 25.3 | Small tools | N | Base | Adder kept as separate line per brief
T5-06 | 1A | Both buildings | Commissioning | Final test + commissioning: TMV certs x11, RPZD tests, HWU, Form 72, handover docs | 1 | item | 4 days | Estimator judgement + subbie rates (Form 72 $350; hydro gear $450/d) | M | Crew 5 Fit-Off / Misc | 3 | 4 | 4 | 120 | 33.7 | Test gear (subbie) | N | Base
T5-07 | 1A | Sitewide | QA | As-cons + ADAC XML - TPS water/sewer/fire assets | 1 | item | 3 days | Estimator judgement - surveyor subbie $180/hr attendance + drafting | M | Crew 5 Fit-Off / Misc | 3 | 3 | 3 | 90 | 25.3 | Surveyor 2d | N | Base | Plumbing approval LODGEMENT excluded (X2) - attendance at BA inspections still allowed here
ROLL-UP |  |  |  | TPS (Hydraulic) BASE total | [7 empty] | 166 | 166 | 4980 | 1400 |  |  |  | Stage 1A 146 cd / Stage 1B 20 cd; crews of 3 (2 Trades + 1 TA); LH supervision 140 days x 10 hr
ROLL-UP |  |  |  | TPS (Hydraulic) EBC (excluded from base) | [7 empty] | 2 | 2 | 60 | 0 |  |  |  | T1-06 Ø100/DN110 rising main pumpwell->dischar
INDICATIVE LABOUR $ (clearly marked - indicative @ uplifted rates: LH $132.9634/hr, Trades $101.6458/hr, TA $82.9510/hr, ex GST)
|  |  |  | Crew labour (base) | [14 empty] | 166 cd x $2,862.43 = $475,163
|  |  |  | Supervision (LH) | [14 empty] | 140 d x $1,329.63 = $186,149
|  |  |  | TOTAL indicative labour | [14 empty] | $661,311 ex GST - INDICATIVE ONLY, pricing at Phase 6
PLANT ROLL-UP (dry hire unless noted; day rates ex GST from Equip_HIRE registers - header says WEEKLY (5 day) but unit column says Day: treated as $/day, FLAGGED for Phase 6 confirmation)
Item | Total days | Indicative rate/day | Source | Flag
13-16T excavator | 16 | $317.20 | Hyd Equip_HIRE_Master | Ø200/125 mains + fire main
8T excavator | 6 | $261.17 | Hyd Equip_HIRE_Master | Tapping/booster/meter
3-5T excavator | 17 | $238.67 | Hyd Equip_HIRE_Master | Sewer/TW/GIT
1.8T excavator | 24 | $137.14 | Hyd Equip_HIRE_Master | Under-slab UG + stubs + branches
PE butt welder + EF processor | 22 | ALLOWANCE ~$350/d | NOT in hire registers | HDPE Ø200/125 mains + trade waste - quote at Phase 6
Trench roller dbl drum | 22 | $165.00 | Hyd Equip_HIRE_Master
Upright rammer/wacker | 28 | $34.29 | Hyd Equip_HIRE_Master
<6T tipper | 18 | $171.43 | Hyd Equip_HIRE_Master
Hydro-excavation truck | 2 | $190/hr wet (3000L) | Misc Subbie Rates | Ø300 live main + existing MH exposure
Scissor lift <26ft | 13 | $89-150/wk | Civ Equip_HIRE (weekly) | Seismic + AG rough-in
Water truck (test/flush cartage) | 3 | $110/hr wet | Misc Subbie Rates | No site water - ITT S17.3; potable storage pods extra
Crane truck / HIAB | 3 | ALLOWANCE ~$180/hr | Estimator allowance | Booster, GIT, HWU deliveries
Test pump/hydro gear | per test | $1,945 full hydro / $3,560 boost / $450 gear | Misc Subbie Rates | 3 site systems + buildings

## TCS_Programme
ID | Activity | Crew | Start (work day) | Finish (work day) | Duration (days) | Month (÷21) | Predecessor / logic
M0 | MILESTONE: Letter of acceptance + 14-day possession (ITT S20) | - | - | - | - | - | Contract
M1 | GATE: EDQ Conditions 16/17 approval (20 business days) - ASSUMED cleared by possession; slip covered by A-11 | - | - | - | - | - | RPT006_B S3.1
M2 | GATE: Clearing + fauna spotter + TPZ fencing complete BY OTHERS (VFMP staging) | - | - | - | - | - | VFMP; machinery curfew 6pm-6am = 10-hr days must sit inside 6am-6pm, zero daylight float
A-01 | TCS establishment | Civil Crew A | 1 | 3 | 3 | M1 | After possession
A-02 | Set-out + locate | Civil Crew A | 4 | 5 | 2 | M1 | A-01
C-01 | C10 2700x1200 basin outlet (crane) | Civil Crew C | 6 | 11 | 6 | M1 | Outfall first
A-03 | RCP375 CL3 mainline 702.9 m | Civil Crew A | 6 | 21 | 16 | M1 | A-02
A-04 | RCP375 CL4 + RCP600 | Civil Crew A | 22 | 22 | 1 | M2 | A-03
A-05 | PP collectors 486.6 m | Civil Crew A | 23 | 32 | 10 | M2 | A-04; before courts pavement
A-06 | 225 DWV line 81 | Civil Crew A | 33 | 34 | 2 | M2 | A-05
A-07 | 100 DWV laterals | Civil Crew A | 35 | 38 | 4 | M2 | A-06
A-08 | Rock extra-over allowance (window) | Civil Crew A | 6 | 38 | 33 | M1-M2 | Concurrent allowance across trenching
B-01 | RGU inlets x33 | Civil Crew B | 11 | 32 | 22 | M1-M2 | Follows mainline 5d lag
B-02 | 1050 chambers x13 | Civil Crew B | 33 | 45 | 13 | M2-M3 | B-01
B-03 | 1200 chambers x4 (26-02 upstand) | Civil Crew B | 46 | 51 | 6 | M3 | B-02
B-04 | Field inlets x3 | Civil Crew B | 52 | 53 | 2 | M3 | B-03
B-05 | Pipe-to-pipe connections x20 | Civil Crew B | 54 | 60 | 7 | M3 | B-04
B-06 | Pipe headwalls x10 | Civil Crew B | 61 | 70 | 10 | M3-M4 | B-05
B-08 | Rock pads 513 m2 | Civil Crew B | 71 | 79 | 9 | M4 | B-06
B-07 | Concrete spillway 50 m | Civil Crew B | 81 | 90 | 10 | M4-M5 | B-08; basin shaping by others complete
B-09 | Kerb chutes x9 (EBC - unscheduled pending D6-F1) | Civil Crew B | - | - | - | - | If reinstated: with B-06 window
C-02 | Small culverts 66.4 m | Civil Crew C | 12 | 20 | 9 | M1 | C-01
C-03 | RCBC 1200/1500 46.8 m | Civil Crew C | 21 | 28 | 8 | M1-M2 | C-02
C-04 | Culvert headwalls x20 | Civil Crew C | 29 | 44 | 16 | M2-M3 | C-03
C-05 | WSUD DN3300 + cartridges | Civil Crew C | 45 | 52 | 8 | M3 | C-04; EDQ Cond 16; cartridge delivery
M3 | GATE: Courts pavement complete BY OTHERS - ASSUMED day 84 | - | 84 | 84 | 1 | M4 | Builder programme assumption
C-06 | GT1-4,7-9 trench drains 561.9 m | Civil Crew C | 85 | 107 | 23 | M5-M6 | M3
C-07 | Trash boxes x25 + laterals | Civil Crew C | 108 | 120 | 13 | M6 | C-06
A-12 | 1B establishment/remob | Civil Crew A | 98 | 99 | 2 | M5 | 1B area released (assumed)
C-08 | 1B GT5+GT6 46.6 m | Civil Crew C | 100 | 102 | 3 | M5 | A-12 (crew C splits)
C-09 | 1B lines 60/61/83 + TB100 x4 | Civil Crew C | 103 | 106 | 4 | M5-M6 | C-08
A-09 | Testing + CCTV attendance | Civil Crew A | 108 | 111 | 4 | M6 | Drainage complete
A-13 | 1B testing/CCTV/ADAC | Civil Crew A | 112 | 113 | 2 | M6 | C-09
A-10 | As-cons + ADAC | Civil Crew A | 115 | 117 | 3 | M6 | A-09
A-11 | EDQ-gate remob allowance (unscheduled) | Civil Crew A | - | - | - | - | Risk line
M4 | PRACTICAL COMPLETION TCS - working day ~120 (approx 6 months elapsed incl 5-day weather allowance + PH/RDO) | - | 120 | 120 | 1 | M6
BASIS: work days are roster #3 10-hr days, 6-day week, 21 work-days/month. Programme = ~120 work days = ~5.7 roster months; carry 6 months elapsed incl ITT S20.h 5-day weather/latent allowance + 2027 QLD public holidays.
HOLIDAYS/RDO ASSUMPTION: 2027 QLD public holidays (approx 12 incl Rockhampton Show Day) and industry RDOs assumed absorbed in the 21-work-day month convention (26 possible 6-day-week days less ~5 for PH/RDO/travel); fly-home every 2nd weekend per roster #3.
CURFEW: VFMP machinery curfew 6pm-6am - the 10-hr day must sit 6:30am-5:30pm approx; NO extended-hours recovery available after weather events (flagged as programme risk).
SEQUENCE vs VOL 20: 1A first; outfall (C10) and trunk lines early; courts collectors before pavement; GT trench drains AFTER courts pavement by others (assumed day 85); 1B (GT5/GT6, lines 60/61/83) in a late window off Crew C.
GATES: EDQ Conditions 16/17 (20-business-day reviews) gate stormwater start - remobilisation allowance A-11 carried as a line, not spread. Clearing/fauna spotter/TPZ fencing by others precede possession of each work front.
LONG-LEAD FLAGS: Ocean Protect StormFilter cartridges + DN3300 manhole (PC supply - 12+ wks); RCBC 2700x1200 special units (12-16 wks); Hauraton Recyfix GT + trash boxes import (10-16 wks); precast headwall/RGU schedule releases at award.
ITP WITNESS/HOLD POINTS (estimate for S20 programme): TCS approx 38 witness + 12 hold = 50 (per-line bedding/pre-backfill, pit bases, geotech >1.5 m entry inspections at WSUD/C10, CCTV reviews, compaction lots, pre-PC drainage clean per S24).
5-DAY WEATHER/LATENT (ITT S20.h): carried as float at programme end - NOT costed into productivity rates; wet-season seepage risk (geotech S4.2) sits against Feb-Mar work fronts if 2027 start slips.

## TPS_Programme
ID | Activity | Crew | Start (work day) | Finish (work day) | Duration (days) | Month (÷21) | Predecessor / logic
M0 | MILESTONE: Letter of acceptance + 14-day possession (ITT S20) | - | - | - | - | - | Contract
T1-01 | TPS establishment | Crew 1 | 1 | 3 | 3 | M1 | After possession
T1-02 | Set-out + locate | Crew 1 | 4 | 5 | 2 | M1 | T1-01
T1-03 | Site gravity sewer 207.5 m | Crew 1 | 6 | 11 | 6 | M1 | T1-02
T1-04 | SMS x2 + property connection | Crew 1 | 12 | 14 | 3 | M1 | T1-03; FRW attendance
T1-05 | Site TW run + storm stubs | Crew 1 | 15 | 16 | 2 | M1 | T1-04
T2-01 | Ø200 HDPE main 134.6 m | Crew 2 | 6 | 10 | 5 | M1 | T1-02
T2-02 | Ø300 tapping cluster | Crew 2 | 11 | 13 | 3 | M1 | T2-01; FRW shutdown window
T2-03 | Meter assemblies + slab | Crew 2 | 14 | 17 | 4 | M1 | T2-02; congestion at meter slab
T2-04 | 125 PE CW spine 236.9 m | Crew 2 | 18 | 23 | 6 | M1-M2 | T2-03
T2-05 | CW take-off sets | Crew 2 | 24 | 26 | 3 | M2 | T2-04
T2-06 | 32/25 PE branches | Crew 2 | 27 | 28 | 2 | M2 | T2-05
T2-07 | 125 REDLINE fire main 217.7 m | Crew 2 | 29 | 33 | 5 | M2 | T2-06
T2-08 | Booster + cabinet + hydrant | Crew 2 | 34 | 36 | 3 | M2 | T2-07
T1-06 | Rising main 110 m (EBC - unscheduled pending RFI) | Crew 1 | - | - | - | - | CL C4
M1 | GATE: NBC bored piers + ground beams complete BY BUILDER - ASSUMED day 63 (month 3) | - | 63 | 63 | 1 | M3 | Builder programme assumption
T1-07 | NBC UG drainage 268 m | Crew 1 | 64 | 77 | 14 | M4 | M1; pre-slab
T1-08 | NBC UG trade waste + GIT | Crew 1 | 78 | 85 | 8 | M4-M5 | T1-07
T1-10 | DP stubs NBC 19 + PAM 4 | Crew 1 | 86 | 89 | 4 | M5 | T1-08 (PAM share later if structure lags)
M2 | GATE: NBC frame/roof + internal walls set-out BY BUILDER - ASSUMED day 105 (month 5) | - | 105 | 105 | 1 | M5 | Builder programme assumption
T3-01 | NBC stacks + 13 vent risers | Crew 3 | 106 | 111 | 6 | M6 | M2; roofer coordination
T4-01 | NBC water rough-in 437.6 m | Crew 4 | 106 | 117 | 12 | M6 | M2
T3-02 | NBC AG waste + tundishes | Crew 3 | 112 | 116 | 5 | M6 | T3-01
T3-04 | Seismic restraint - drainage | Crew 3 | 117 | 119 | 3 | M6 | T3-02
T4-02 | TMV/RPZD/valve sets | Crew 4 | 118 | 120 | 3 | M6 | T4-01
T4-03 | HWUs + HW loop | Crew 4 | 121 | 123 | 3 | M6 | T4-02
T4-04 | FHR + FB | Crew 4 | 124 | 124 | 1 | M6 | T4-03
T4-07 | Seismic restraint - water | Crew 4 | 125 | 126 | 2 | M6 | T4-04
T5-05 | Articulation joints adder | Crew 5 | 106 | 108 | 3 | M6 | With rough-in start
M3 | GATE: PAM structure available BY BUILDER - ASSUMED day 147 (month 7) | - | 147 | 147 | 1 | M7 | Builder programme assumption
T1-09 | PAM UG drainage 68 m | Crew 1 | 148 | 151 | 4 | M8 | M3
T2-09 | 1B branch take-offs + bubbler services | Crew 2 | 148 | 151 | 4 | M8 | M3 (crew 2 remob)
T3-03 | PAM vent + AG waste | Crew 3 | 152 | 153 | 2 | M8 | T1-09
T4-05 | PAM water rough-in 65.5 m | Crew 4 | 152 | 155 | 4 | M8 | T1-09
T4-06 | PAM HWU + TMV + check meter | Crew 4 | 156 | 156 | 1 | M8 | T4-05
T2-10 | Hydro test + disinfection (water carted) | Crew 2 | 156 | 159 | 4 | M8 | Mains + buildings loop-able
T1-11 | CCTV + testing - sewer/drainage | Crew 1 | 160 | 162 | 3 | M8 | All UG complete
M4 | GATE: NBC wet areas ready for fit-off BY BUILDER - ASSUMED day 168 (month 8) | - | 168 | 168 | 1 | M8 | Builder programme assumption
T5-01 | NBC fixture fit-off ~93 EA | Crew 5 | 169 | 181 | 13 | M9 | M4
T5-02 | Kitchen specialties + Billi + GIT comm. | Crew 5 | 182 | 184 | 3 | M9 | T5-01
T5-03 | PAM fit-off | Crew 5 | 185 | 188 | 4 | M9 | PAM wet areas ready (assumed)
T5-04a | ODF x2 (NBC external) | Crew 5 | 189 | 189 | 1 | M9 | Paving by others complete
T5-04b | 1B bubbler stations | Crew 5 | 190 | 190 | 1 | M10 | T5-04a
T5-06 | Commissioning + Form 72 | Crew 5 | 191 | 194 | 4 | M10 | All systems live
T5-07 | As-cons + ADAC XML | Crew 5 | 195 | 197 | 3 | M10 | T5-06
T1-12 | Remobilisation allowance (unscheduled) | Crew 1 | - | - | - | - | Risk line
M5 | PRACTICAL COMPLETION TPS - working day ~197 (approx 10 months elapsed incl weather/PH; 3 discrete site windows) | - | 197 | 197 | 1 | M10
BASIS: as TCS - roster #3, 21 work-days/month. Programme = ~197 work days = ~9.4 roster months across THREE discrete site windows (site mains M1-2; building rough-in M4-8; fit-off M9-10); carry 10 months elapsed incl 5-day weather allowance + PH.
BUILDER-WINDOW ASSUMPTIONS (stated per brief - TPS building work follows builder structure): NBC piers/ground beams complete day 63 (month 3); NBC frame/roof day 105 (month 5); PAM structure day 147 (month 7); NBC wet areas fit-off-ready day 168 (month 8). Any slip moves TPS windows 1:1 - remob allowance T1-12 carried.
MAINS-THROUGH-1B RULE: 1A item 2.1 mains run through 1B land priced/programmed in 1A (T2-01..T2-08); 1B's own branch take-offs (T2-09) in the 1B window only.
HOLIDAYS/RDO: same convention as TCS (21-day month absorbs approx 12x 2027 QLD PH + RDOs).
NO SITE WATER (ITT S17.3): all test/flush/disinfection water carted + stored (T2-10, T1-11 plant); potable storage and distribution in TPS establishment.
LONG-LEAD FLAGS: 316 SS press-fit pipe/fittings (10-14 wks - conforming water system); HDPE Ø200 SDR11 pipe + large EF fittings (8-10 wks); 150 H-pattern booster assembly + cabinet (10-12 wks); Rheem 315L x2 (4-6 wks); Stoddart s/s fixtures + in-wall cisterns (8-12 wks); Tradelink quote expires 13/08/26 - escalation qualification.
ITP WITNESS/HOLD POINTS (estimate): TPS approx 30 witness + 12 hold = 42 (tapping shutdown, pressure tests x3 site systems + 2 buildings, disinfection, sewer air/water tests, GIT install, TMV commissioning x11, boost/hydro tests, Form 72, per-building rough-in cover inspections).
EBC LINES: rising main T1-06 and FE extinguishers excluded from base; kerbside note - plumbing approval lodgement excluded (X2) but BA inspection attendance is inside T5-06/T5-07.

## Accommodation
Entity | Month | Persons on site (incl LH) | Crews present | Apartments needed (3/apt) | Apartment cost (ex GST) | Individual nights (25/pers-mo) | Individual cost (ex GST)
TCS | M1 | 10 | A+B+C+LH | 3 | 13818.18 | 250 | 25811.7
TCS | M2 | 10 | A+B+C+LH | 3 | 13818.18 | 250 | 25811.7
TCS | M3 | 7 | B+C+LH | 2 | 9212.12 | 175 | 18068.19
TCS | M4 | 4 | B+LH | 1 | 4606.06 | 100 | 10324.68
TCS | M5 | 7 | B+C+LH | 2 | 9212.12 | 175 | 18068.19
TCS | M6 | 7 | A+C+LH | 2 | 9212.12 | 175 | 18068.19
TCS | TOTAL | 45 person-months |  | 13 apt-months | 59878.79 | 1125 | 116152.65
TCS | OPTION A - apartments (crews) + LH individual |  |  |  | $75,366 |  | RECOMMENDED - apartments house 3; LH on nightly individual
TCS | OPTION B - all individual nightly |  |  |  | $116,153 |  | Premium ${optB-optA:,.0f} vs Option A
TPS | M1 | 7 | 1+2+LH | 2 | 9212.12 | 175 | 18068.19
TPS | M2 | 7 | 1+2+LH | 2 | 9212.12 | 175 | 18068.19
TPS | M3 | 4 | 1+LH | 1 | 4606.06 | 100 | 10324.68
TPS | M4 | 4 | 1+LH | 1 | 4606.06 | 100 | 10324.68
TPS | M5 | 0 | gap - awaiting builder | 0 | 0 | 0 | 0
TPS | M6 | 7 | 3+4+LH | 2 | 9212.12 | 175 | 18068.19
TPS | M7 | 7 | 4+5(early)+LH | 2 | 9212.12 | 175 | 18068.19
TPS | M8 | 7 | 1(PAM)+2+4+LH | 2 | 9212.12 | 175 | 18068.19
TPS | M9 | 4 | 5+LH | 1 | 4606.06 | 100 | 10324.68
TPS | M10 | 4 | 5+LH | 1 | 4606.06 | 100 | 10324.68
TPS | TOTAL | 51 person-months |  | 14 apt-months | 64484.85 | 1275 | 131639.67
TPS | OPTION A - apartments (crews) + LH individual |  |  |  | $87,715 |  | RECOMMENDED - apartments house 3; LH on nightly individual
TPS | OPTION B - all individual nightly |  |  |  | $131,640 |  | Premium ${optB-optA:,.0f} vs Option A
BASIS: Roster Example #3 - 6-day week, 10-hr days, stay Rockhampton weekends, fly home every 2nd weekend; 21 work-days/210 hrs/month.
RATES (Accomodation_Master, ex GST): full apartment/townhouse via agent $4,606.06/month (houses a crew of 3); individual private unit nightly $103.2468. Nights basis 25/person-month (approx 5 nights home per month on 2nd-weekend fly-back) - stated assumption.
FLIGHTS (Misc Rates, not accommodation): $220/flight 1-way; 1 return per person per fortnight cycle - priced in commercial build, flagged here only.
NOTE: no shared accommodation between entities - each entity carries its own block in full (SS5.2).

## Sensitivity
# | Entity | Driver (activity) | Base crew-days | Range | Swing crew-days | Swing crew hrs | Indicative labour $ swing (uplifted rates) | Basis of range
1 | TCS | C-06 GT trench drains 561.9 m (25 m/day) | 23 | +30% / -20% | +6.9 / -4.6 | +207 / -138 | +$19,751 / -$13,167 | L-conf rate; proprietary channel + concrete surround + court-edge tolerance; no comparable CQU workbook rate
2 | TCS | B-01/02/03 pit set (RGU+1050+1200) | 41 | ±25% | ±10.3 | ±308 | ±$29,483 | Pit cycle judgement; rock at pit bases (XW 0.2-2.2 m at 6 geotech pits) hits pits before trenches
3 | TCS | Culvert install C-01/02/03 (130.8 m RCBC) | 23 | ±30% | ±6.9 | ±207 | ±$19,751 | Zero-cover tie-ins + heavy lifts; extra-over excavation/bedding still unpriced (NewItems #2 - Phase 6)
4 | TCS | A-08 rock extra-over allowance | 10 | +100% / -50% | +10 / -5 | +300 / -150 | +$28,624 / -$14,312 | 25/36 refusal but no borehole-to-alignment overlay; ITT S18.2 written-direction regime may not fund production loss
5 | TCS | A-03 RCP375 mainline (45 m/day) | 16 | ±25% | ±4.0 | ±120 | ±$11,450 | Flat-grade laser penalty judgement; weather-exposed open field runs
6 | TCS | C-05 WSUD DN3300 manhole | 8 | +40% / -25% | +3.2 / -2.0 | +96 / -60 | +$9,160 / -$5,725 | Deepest excavation; founding depth not shown on long sections; wet-season seepage; geotech entry inspections
7 | TPS | T5-01 NBC fixture fit-off (~93 EA) | 13 | +35% / -15% | +4.6 / -2.0 | +137 / -59 | +$13,022 / -$5,582 | Fixture counts L-confidence - Phase 4 recount AR-NBC-3006-3009 + Tradelink reconciliation mandatory before pricing
8 | TPS | T1-07 NBC UG drainage (20 m/day) | 14 | ±30% | ±4.2 | ±126 | ±$12,022 | Pier/ground-beam congestion + articulation on H1 'P' site; builder slab-cycle interference
9 | TPS | T4-01 NBC water rough-in (38 m/day) | 12 | +25% / -15% | +3.0 / -1.8 | +90 / -54 | +$8,587 / -$5,152 | Conforming 316 SS press-fit regime slower than copper alternate (both priced per SS5.5); blockwork coordination
10 | TPS | T2-01..T2-08 site water/fire mains | 31 | ±20% | ±6.2 | ±186 | ±$17,747 | PE welding weather sensitivity; congestion at meter slab; FRW shutdown windows for tapping
TOTAL POTENTIAL SWING (all drivers, worst case simultaneous - not probabilistic): TCS +41.3/-22.5 crew-days; TPS +18.0/-9.0 crew-days. At $2,862.43/crew-day: TCS +$118k/-$64k; TPS +$52k/-$26k indicative.
L-CONFIDENCE PRODUCTIVITY RATES REGISTER (every rate marked L above and in Activities sheets):
TCS A-08 rock extra-over band - no borehole/alignment overlay exists (geotech gave no elevations); allowance only.
TCS B-07 concrete spillway 5 m/day - allocation RFI + Director (Opens #26); basin embankment design not final.
TCS B-09 kerb chutes (EBC) - D6-F1 undecided; both positions costed.
TCS C-05 WSUD manhole 8 days - founding depth unknown; supply is PC so install interface with Ocean Protect unconfirmed.
TCS C-06 GT trench drains 25 m/day - no benchmark; concrete surround detail from F1320 not re-verified at this phase.
TCS A-11 EDQ-gate remobilisation - gate timing outside our control.
TPS T1-06 rising main (EBC) - discharge point RFI CL C4.
TPS T1-10 DP stubs 6/day on a count of 19+4 that is itself L-confidence (Opens #23).
TPS T3-01 vent risers 2.2/day on a 13-riser ALLOWANCE (verticals never drawn - NewItems #7).
TPS T3-04/T4-07 seismic restraint days - restraint layout not designed (install + drafting only, CL C7).
TPS T5-01 fit-off 7 EA/day against L-confidence counts (Phase 4 recount mandatory).
TPS T5-04b bubbler stations - units undefined in legend (CL C10).
TPS T5-05 articulation adder - joint count deferred to Phase 6 (NewItems #12).